## SUM
SBI LIFE INSURANCE CO LTD
PROPOSED INTERIOR, ELECTRICAL, HVAC, FIRE ALARM, SPRINKLER SYSTEM, WORKS FOR SBI LIFE, REGIONAL OFFICE AT KODAMBAKKAM, CHENNAI
SUMMARY
S.NO | DESCRIPTION | AMOUNT IN INR
I | INTERIOR WORKS
II | ELECTRICAL WORKS
III | LIGHT FIXTURES
IV | HVAC WORKS
V | FIRE ALARM WORKS
VI | SPRINKLER SYSTEM
GRAND TOTAL
Signature of the Tendrer :
Address :
Date :

## i
SBI LIFE INSURANCE CO LTD
PROPOSED INTERIOR WORKS FOR SBI LIFE, REGIONAL OFFICE AT KODAMBAKKAM, CHENNAI
BILL OF QUANTITIES - INTERIOR WORKS
a | All the com.ply used is of MR grade - IS 303: 1989 only
b | All concealed faces of ply to be painted with one coat of wood preservative paint.
c | Table Drawer, storage and cupboard inside should be finished with 0.8mm thick laminate of approved colour and shade.
d | All exposed faces of TW/Steam beech beading/ lipping should be melamine polished and tinted to required shade as directed by the Client/ Architect.
e | All com. ply free edges should be provided with TW lipping alround.
f | Size of framework indicated should be finished size.
g | Furniture joints should be in Tonge and groove
h | Cost should include for providing grooves in laminate, veneer as shown in drawing and TW/ Steam beech beadings wherever shown should be included.
i | All the Carpentry work must be executed only in site after getting the Materials approved from Client/Architect.
j | Modular Type of Furniture work is not acceptable.
k | Company supply letter should be Submitted for ply wood laminate, Blinds, Aluminium Frame, Hardware, Veneer, False ceiling during the submission of bill.
l | Necessary mock ups shall be shown by the vendor prior to award of the package at no additional cost
m | Rate to include cost of transportation ,handling ,replacement etc.;
n | The furniture's for all locations/ rooms shall be resized (if required) individually based on the available site dimensions at no additional cost.
o | The Contractor shall engage an independent Housekeeping – debris removal agency on a day-to-day basis. Hence Contractor would be responsible for cleaning up the debris and waste materials accrued from his/others work and dispose the accumulated debris on a daily basis. This amount will be charged to all vendor by pro rata basis
S. No. | Description | Qty | Unit | Rate | Amount
1 | Dismantling 230mm Brick Work
| Dismantling existing 230mm thick brick walls in CM including the plaster finish and lintels and removing the debris clear off the premises as directed by the Client / Architect. | 11 | Cum
2 | Salvage-Remove Existing Partition, Storage, including sanitary fixtures, pipe lines, Electrical wiring, sockets etc and clear the debris away from the site | -245 | Sqm
3 | Alteration in Existing Partition with necessary Re-lamination etc complete | 21 | Sqm
4 | Low Level Partition - Laminate Finish
Providing and fixing low level partition 1200mm high to shape as per drg. comprising.
Aluminium frame work of size 50 x 50 x 2mm (1.037kg/m) at about 600mm centres vertically and 3 Nos. horizontally of the same section at floor level, 750mm level and 1200mm level. 8mm com. ply on both side of the frame work and to be finished with 1mm thick laminate of approved colour and shade with grooves. Top of the partition finished with 15mm thick and 75mm wide steam beech moulding and finished with melamine polish. 12mm thick clear float glass with necessary 3M etching to shape and fixed with 75 x 15mm steam beech moulding.
| All exposed faces of steam beech beading are to be polished to the satisfaction of the Client/ Architect. | 183 | Sqm
5 | Sliding & Folding partition - veneer finish
Sliding & Folding partition - veneer finish with Acoustical sound proof.
| Operable wall consisting of 100 mm thick individually movable elements, suspended from a top track only, each panel to have top and bottom operable pressure seals operated by a crank handle to ensure optimum contact pressure up to 800N. The elements must be inter-connected by means of a positive locking concave/convex aluminium profile integrated with magnetic profile having a linear attraction of 40 N/m. Elements must be constructed of a non-deflecting steel tube frame and aluminium profiles, bolted together. The frame must be clad either side with 16 mm MDF panels hung in acoustic isolation from the frame and allowed to vibrate independently of the frame. The facia panels must also be easily removable. The panel must be filled with high density rock wool in accordance with the specified sound insulation requirements. The telescopic element must open and close 120 mm and must be operated by a single mechanism for both the top and bottom seals. Rate should be inclussive of 3.5mm thick veneer and melamine polish of approved colour and shade | 23 | Sqm
6 | Sliding & Folding partition - Laminate finish Laminate
Sliding & Folding partition - Laminate with Acoustical sound proof.
| Operable wall consisting of 100 mm thick individually movable elements, suspended from a top track only, each panel to have top and bottom operable pressure seals operated by a crank handle to ensure optimum contact pressure up to 800N. The elements must be inter-connected by means of a positive locking concave/convex aluminium profile integrated with magnetic profile having a linear attraction of 40 N/m. Elements must be constructed of a non-deflecting steel tube frame and aluminium profiles, bolted together. The frame must be clad either side with 16 mm MDF panels hung in acoustic isolation from the frame and allowed to vibrate independently of the frame. The facia panels must also be easily removable. The panel must be filled with high density rock wool in accordance with the specified sound insulation requirements. The telescopic element must open and close 120 mm and must be operated by a single mechanism for both the top and bottom seals. | 18 | Sqm
6 | Solid Partition - Laminate Finish
Providing and fixing double skin full height partition to detail as per drawing.
(a) Frame work: Aluminium frames of 50 x 50 x 2mm thick (1.037 kg/m), vertically at about 600mm centres varied along columns wall ends, junctions of walls, as necessary. Horizontally of same size of frame at floor level,450mm, 900mm, 1500mm, 2100mm and roof level fixed in position. The vertical frames fixed to soffit of slab with necessary screws, MS clamps, rawl plugs, expansion fasteners, etc., complete.
(b) Lining Work: 8 mm com. ply on both sides of framework from floor level to false ceiling level and to be finished with 1mm thick laminate of approved colour and shade on both sides including necessary grooves and Steam beech beadings.
(c) Providing Flush door 35mm thick (finished) flush shutters with external lipping, phenol formaldehyde bonding and finished with 1mm thick laminate of approved colour & shade on both side with necessary grooves. Dorma or equivalent make hardware fittings like locking arrangements, 22mm dia & 300mm high SS brush finish handles, door closer, Hinges, SS Tower Bolts, SS door stopper, etc. fixed to the shutters.Rate should be inclussive of Steam Beach Beeding of Size 35 x 10mm all around the Door shutter and finished with Melamine Polish over the coat of sealer.
All exposed faces of Steam beech beading to be polished with melamine to the satisfaction of the Client/ Architect.
| Note: Measurement for the partition area shall be considered from floor level to false ceiling level only. | 130 | Sqm
7 | Solid Partition-One side Veneer one side Laminate Finish
Same as above but 6mm com. ply at inside and 8mm com.ply at out side of framework from floor level to false ceiling level and to be finished with 3.5mm thick veneer with melamine polish at inside and 1mm thick laminate of approved colour and shade on outside, including necessary grooves and Steam beech beadings.
Providing and fixing Flush door with 34.5mm thick (finished) flush shutters with external lipping, phenol formaldehyde bonding and finished with 3.5mm thick veneer on one side & 1mm thick laminate of approved colour & shade on other side with necessary grooves. Dorma or equivalent make hardware fittings like locking arrangements, 22mm dia & 300mm high SS brush finish handles, door closer, Hinges, SS Tower Bolts, ss door stopper etc. fixed to the shutters. Basic cost of veneer should not be less than Rs.865/sqm. Rate should be inclussive of Steam Beach Beeding of Size 35 x 10mm all around the Door shutter and finished with Melamine Polish over the coat of sealer.
All exposed faces of Steam beech beading to be polished with melamine to the satisfaction of the Client/ Architect.
| Note: Measurement for the partition area shall be considered from floor level to false ceiling level only. | 120 | Sqm
8 | 115mm thick Brick Work
| Half brick masonry 115mm thick partition walls in CM 1:4 using bricks of strength 35 Kg/Sq.cm, reinforced with hoop iron 25mm by 15 gauge at every 4th course or 2 nos of 6 mm dia MS round rods at every 4th course embedded in CM including scaffolding, staging, curing, etc.,complete. | 103 | Sqm
9 | wall Plastering 1:4
| Prepare surfaces and providing and applying plaster with CM 1:4 (1 cement: 4 fine sand) 12mm thick to all interior faces of walls contiguous to masonry in all floors. Rate should be including scaffolding, stagging and curing etc. complete. | 206 | Sqm
10 | Vitrified Tile Flooring
| Providing and fixing 1st quality Vitrified tiles (600 x 600mm) of approved make and shade, over the existing flooring with Cement Mortar 1:5 / Bal Adhesive or equivalent and finished neatly to the manufacturers specifications. (Basic cost of Tile Rs.750/Sqm). Rate should be included necessary skirting & Dismandling the Existing Flooring etc complete. | 158 | Sqm
11 | Ceramic Tile Flooring
| Providing and fixing Kajaria Make Power line series / Rock stone Beige or Equivalant tile flooring of size 300mm x 300mm over and including a 20mm thick base of CM (1:3) (1 cement: 3 Coarse sand) finished neatly to manufacturer's specifictions. (Basic cost of Tile Rs.900/sqm ) | 5 | Sqm
12 | Dado on walls
| Dado on walls with Approved Make or Equavalent Joint free tile of size 300 X 450mm of minimum thickness 7mm set with paper thin joints, over and including a 12mm hick base of CM 1:3 (1 cement : 3 coarse sand) with white cement slurry, to specification in:( Basic cost of tile should not be less than Rs.700/sqm). The corners to be finished with Dural Nosing. Rate should be including chipping the existing brick wall, plastering and clearing the debris away from the site as directed by the Client / Architect. | 67 | Sqm
13 | Brick Jelly concrete filling
| Providing and filling brick jelly concrete in Toilet sunken area with necessary chemical mixing plastering type water proofing treatment etc complete. Rate Should be inclusive of dismantling the existing flooring and brick jelly concrete & clearing the debris away from the site as directed by the Client / Architect. | 2 | Cum
14 | Water Proofing
(i) Ist course of applying cement slurry @ 4.4 kg/sqm mixed with water proofing compound conforming to IS 2645 in recommended proportions including rounding off junction of vertical and horizontal surface.
| (ii) IInd course of 20 mm cement plaster 1:3 (1 cement : 3 coarse sand) mixed with water proofing compound in recommended proportion including rounding off junction of vertical and horizontal surface. | 7 | Sqm
15 | Partly Glazed & Partly Panelled Partition
Providing and fixing double skin partition, partly panelled and partly glazed to detail as per drawing.
(a) Frame work: Aluminium frames of 50 x 50 x 2mm thick (1.037kg/m), vertically at about 600mm centres varied along columns wall ends, junctions of walls, as necessary. Horizontally of same size of frame at floor level, 450mm 900mm, 2100mm and roof level. The vertical frames fixed to soffit of slab with necessary screws, MS clamps, rawl plugs, expansion fasteners, etc., complete.
(b) Lining Work: 8 mm com. ply on both sides of framework from floor level to 900 mm level and 2100 mm level to false ceiling level finished with 1mm thick laminate of approved colour and shade. Between 900mm and 2100mm level, 8mm thick clear float glass with 3M etching fixed over steam beech beading of size 35 x 10mm thick all around the glass panels on both side.
(c) Providing and fixing partly panelled and partly glazed door in partition 35mm thick (finished) flush shutter finished with 1mm thick laminate of approved colour & shade on both sides with necessary grooves, 8mm thick plain glass with necessary steam beech beading and 3M etching. Dorma or equivalent hardware fittings like locking arrangements 22mm dia and 300mm long SS brush finish handles, door closer, hinges, SS Tower Bolts, SS door stopper, etc., to be fixed to the shutters. Rate should be inclusive of Steam Beach Beeding of Size 35 x 10mm all around the Door shutter and finished with Melamine Polish over the coat of sealer.
All exposed faces of Steam beech beading to be polished with melamine to the satisfaction of the Client/ Architect.
| Note: Measurement for the partition area shall be considered from floor level to false ceiling level only. | 121 | Sqm
16 | Fully Glazed - Fixed Glass Partition with Patch Fitting
Providing and fixing of fixed glass partitions with 12mm thick toughened glass using PT Standard fittings like PT 90/PT 92 of Ozone or Equivalent make at the top and bottom including cutting, making holes in glass and fixing the fittings in floors, ceilings etc and making the same good with necessary screws, sealants wherever required. Rate should include necessary 3M etching film of approved design and pattern.
| Rate shopul be inclussive of Providing and fixing frameless fully glazed 12mm thk toughened float glass fixed with Dorma or Equivalent make patch fittings including cutting, making holes, cutouts in the glass of required shape and size to accommodate fittings and fixing the fittings in floors, soffits, jams including necessary fixtures, srews, sealent wherever required and SS cover over patch fittings. Rate shall include necessary etching film of approved design and pattern. 1 pair of 600mm long S.S. (C Shape) Handles of approved make, floor springs, and any necessary hardware items. Dorma Top Pivot - PT 24, Top Patch Fittings - PT 20, Bottom Patch fittings - PT 10, Floor Spring - BTS 75 V, Centre Lock US-20, Handle - TG DIH600 - 38mm dia X 600mm length. | 75 | sqm
II | DOORS
17 | Main Entrance Door - Framless - Patch fitting
| Providing and fixing frameless fully glazed 12mm thk toughened float glass fixed with Dorma or Equivalent make patch fittings including cutting, making holes, cutouts in the glass of required shape and size to accommodate fittings and fixing the fittings in floors, soffits, jams including necessary fixtures, srews, 3M etching, sealent wherever required and SS cover over patch fittings. Rate shall include necessary etching film of approved design and pattern. 1 pair of 1000mm long S.S. (C Shape) Handles, of approved make, floor springs, and any necessary hardware items. Dorma Top Pivot - PT 24, Top Patch Fittings - PT 20, Bottom Patch fittings - PT 10, Floor Spring - BTS 75 V, Centre Lock US-20, Handle - TG DIH1000 | 8 | Sqm
18 | Partly Glazed & Partly Panelled Door with frame
| Providing and fixing partly panelled and partly glazed door in partition with second class T.W frame of size 75 x 60mm finished with 2 coats of enamel paint over a coat of primer. 35mm thick (finished) flush shutter finished with 1mm thick laminate of approved colour & shade on both sides with necessary grooves, 8mm thick plain glass with necessary steam beech beading and 3M etching. Dorma or equivalent hardware fittings like locking arrangements 22mm dia and 300mm long SS brush finish handles, door closer, hinges, SS Tower Bolts, SS door stopper, etc., to be fixed to the shutters. Rate should be inclusive of Steam Beach Beeding of Size 35 x 10mm all around the Door shutter and finished with Melamine Polish over the coat of sealer. | 4 | Sqm
19 | Flush Door with frame - Laminate Finish
| Providing and fixing Flush door with second class T.W frame of size 75 x 60mm finished with 2 coats of enamel paint over a coat of primer. 35mm thick (finished) flush shutters external lipping, phenol formaldehyde bonding and finished with 1mm thick laminate of approved colour & shade on both side with necessary grooves. Dorma or equivalent make hardware fittings like locking arrangements, SS Brush Finish Round knob handle, door closer, Hinges, SS Tower Bolts, SS door stopper etc. fixed to the shutters. | 2 | sqm
20 | Existing Flush Door - Laminate Finish
| Providing and fixing 1mm thick laminate of approved colour & shade on both side of Existing door Shutters with necessary grooves. | 5 | Sqm
21 | Metal door (3' x 7')
| Providing and fixing Metal Door with framed of Approved make using Galvanized colour coated steel sections and door leaf made up of double skin colour coated steel sheet of 18 gauge fixed with honey comb paper or rockwool with necessary holdfasts embedded in wall. Doors are fixed with SS Brush finish handles, mortice lock, aldrop, etc. Door can be desingned with vision panel | 2 | Nos
III | FALSE CEILING
22 | Gypsum Board False Ceiling
Providing and fixing seamless ceiling with gypboard of 12.5 mm thick, fixed to the underside of the suspended grid formed of GI perimeter channel of size 20 x 27 x 30 mm (MF 6A) fixed along the wall by using wood screws and metal expansion rawl plugs. The GI intermediate channel of size 45 x 15 x 0.90 mm (MF7) shall be fixed to the suspended strap hanger / GI ceiling angle at intervals not more than 1220 mm. The suspended GI ceiling angle / Strap hanger is to be connected with GI soffit cleat of size 37 x 27 x 25 x 1.6 mm and it should be fixed on the roof slab / beam, by using metal expansion fasteners (wt. Type) of 12.5 mm dia. to a length of 35 mm with 6 mm dia. bolt / screw at top ends.
The GI ceiling section of size 80 x 26 x 0.5 mm (MF 5) is to be provided across the intermediate channel at intervals not more than 457 mm centers at bottom and the same shall be fixed by GI connection clips 2.64 mm dia. at the intersection points. The ends of ceiling section (MF 5) channel by adopting an overlap length of minimum 150 mm, connected with intermediate channel shall be fixed to perimeter channel in insertion. The gypboard shall be fixed to the under side of the suspended grid by using 25 mm long dry wall screws. The joints shall be finished with joint paper tape by using jointing compound of India Gypboard Ltd., and applying over it 3 layers of the filler compound to provide a smooth surface. The ceiling surface shall be painted with three coats of approved first quality acrylic emulsion over a coat of primer etc. complete. The rate shall include making cutouts for tube lights, spot lights, duct doors, for specified size, grills etc. for which no extra will be paid separately.
| Rate shall include providing additional trimming around cutouts for light fittings etc. and grills also for providing additional supports from ceiling where main / cross members are cut for light fittings etc. Rate shall include vertical as well as horizontal surfaces as per detailed drawing. Actual “seen” surface of horizontal and vertical will be measured and paid . | 625 | sqm
23 | Mineral Fibre Board False Ceiling
| Providing & Fixing Of Armstrong or approved eqivalent Mineral Fibre Acoustical Suspended Ceiling System With Fine Fissured (Micro Look) Edge Tiles With Armstrong Silhouette Exposed Grid. Silhouette, Main Runners & Cross Tees to have mitred ends & “birdsmouth” notches to provide mitred cruciform junctions. The tile shall be laid on Armstrong Silhouette profile grid system with 15mm white flanges incorporating a 6mm central reveal in white/black colour and with a web height of 45mm and a load carrying capacity of minimum 15.68 Kgs/M2. | 183 | Sqm
24 | Accoustical False ceiling
| Ecophon ADVANTAGE with 15mm tegular edge, easily demountable tile, manufactured from High density glass wool, with the visible surface be batch painted glass tissue in White and the back of the tile should be covered with glass tissue. The glass wool core of the tiles should be tested and classified as non combustible according to prEN ISO 1182. The system should have Sound Absorption NRC value of 0.9 (according to EN ISO 11654). Tiles should withstand a permanent ambient RH upto 95% at 30 * c without sagging, warping or delaminting (ISO 4611). The light reflectance of the tiles should not be less than 83% | 81 | Sqm
25 | Ply False Ceiling - Laminate Finish
Providing and fixing ply box false ceiling with 18mm thick com ply finished with 1mm thick laminate of approved colour and shade. The grid to be suspended by 8 gauge GI wire from roof slab by anchor fasteners to the slab and level adjuster clip GI wire.
| All concealed faces of com ply finished with one coat of wood preservative paint. Note: Visible area only consider for Measurements | 33 | Sqm
IV | TABLES
26 | Regional Director Table with side unit
Providing and fixing Regional Director table of size 3275 / 1700 x 900 X 750mm high to shape as shown in drawing. Comprising table top out of 18mm com. ply with stiffner of same com. ply 100mm wide below the table and 10 x 39.5mm. Steam Beech moulding to shape along edges.
Table top, Side & Rear made out of 18mm thick com.ply finished with 3.5mm thick veneer and melamine polish of approved colour and shade. Front modesty create a pattern with necessary grooves and finished with 3.5mm thick veneer with melamine polish of approved colour and shade as shown in drawing.
2 Nos of 50mm Dia SS Brush Finish wire manager of approved make and quality.
Two set of 4 drawers about 450mm wide, 712.5 mm high and 600mm deep to shape supported with 18mm com. ply at front, rear and two sides, 12mm thick com.ply for bottom. Drawer unit of size 75mm at top of the drawer, 2-Nos of 150mm at middle, 262.5mm at bottom, 75mm black skirting at bottom of drawer with necessary TW lipping, telescopic drawer slides,Individual locking arrangement, 100mm long brush finish S.S. handles, etc., complete.
Front face of the drawer finished with 3.5mm thick veneer of approved colour and shade with necessary steam beech / TW lipping on the edge of drawer.
Providing and fixing side unit for Regional Director table to detail as per drawing of size approx. 1200mm x 450 x 750mm, 18mm com. ply for top, bottom, sides and One intermediate shelf with necessary SS Bracket and 8mm thick com.ply for Rear. 18mm com. ply stiffner below the top and steam beech moulding of size 10 x 39.5mm along the edges. Side hung shutter in both the panels using 18mm com. ply and finished with 3.5mm thick veneer with melamine polish of approved colour and shade, including all necessary TW lipping, box type hinges, Individual locking arrangement, 100mm long SS brush finish handles, Brass Tower Bolt, etc., complete.
The top surface of unit finished with 3.5mm thick veneer with melamine polish of approved colour and shade.
| All exposed faces of Steam beech beading polished to the satisfaction of the Client/ Architect. The inside faces of drawer and table should be finished with 0.8mm thick laminate of approved colour and shade. Basic cost of veneer should not be less than Rs.865/sqm | 1 | Nos
27 | ASM Table with side unit
Providing and fixing ASM table of size 1800 x 900 X 750 mm to detail as shown in drg to shape comprising table top out of 18mm Comply with stiffner of same comply 100 mm wide below the table top out of 10 x 37 mm Steam Beech moulding to shape along edges.
Table top, sides, Front & Rear made out of 18mm thick Com.Ply finished with 1mm thick laminate of approved colour and shade
50mm Dia SS Brush Finish wire manager of approved make and quality.
One set of 4 drawers about 450mm wide, 712.5 mm high and 600mm deep to shape supported with 18mm com. ply at front, rear and two sides, 12mm thick com.ply for bottom. Drawer unit of size 75mm at top of the drawer, 2-Nos of 150mm at middle, 262.5mm at bottom, 75mm black skirting at bottom of drawer with necessary TW lipping, telescopic drawer slides,Individual locking arrangement, 100mm long brush finish S.S. handles, etc., complete.
Front face of the drawer finished with 1mm thick laminate of approved colour and shade with necessary steam beech / T.W lipping on the edge of drawers.
Providing and fixing side unit for ASM table to detail of size 1000mm x 450mmx750mm comprising table top out of 18mm thick com. ply with 10 x 37 mm Steam beech moulding to shape along edges, 18mm com. ply for , bottom, sides and One intermediate shelf with necessary S.S bracket & 8mm thick com ply for rear. Side hung shutter in both the panels using 18mm com. ply finished with 1mm thick laminate of approved colour and shade including all ncessary T.W lipping. Brass Butt Hinges, Individual locking arrangement, 100mm long SS brush finish handles, SS Tower Bolt, etc., complete.
| All exposed faces of Steam beech beading polished to the satisfaction of the Architects. The inner side of the Drawer and table finished with 0.8mm Laminate of approved colour and shade. | 4 | Nos
28 | Officer Table with side unit (1650 x 750 )
Providing and fixing Officer Table table of size 1650 x 750 X 750mm to detail as shown in drg to shape comprising table top out of 18mm Comply with stiffner of same comply 100 mm wide below the table tob out of 10 x 37 mm Steam Beech moulding to shape along edges.
Table top, sides & Front of drawer finished with 1mm thk laminate of approved colour & shade.
50mm Dia SS Brush Finish wire manager of approved make and quality.
One set of 4 drawers about 450mm wide, 712.5 mm high and 600mm deep to shape supported with 18mm com. ply at front, rear and two sides, 12mm thick com.ply for bottom. Drawer unit of size 75mm at top of the drawer, 2-Nos of 150mm at middle, 262.5mm at bottom, 75mm black skirting at bottom of drawer with necessary TW lipping, telescopic drawer slides,Individual locking arrangement, 100mm long brush finish S.S. handles, etc., complete.
Front face of the drawer finished with 1mm thick laminate of approved colour and shade with necessary steam beech / T.W lipping on the edge of drawers.
Providing and fixing side unit for Officer table to detail of size 1000mm x 450mmx750mm comprising table top out of 18mm thick com. ply with 10 x 37 mm Steam beech moulding to shape along edges, 18mm com. ply for , bottom, sides and One intermediate shelf with necessary S.S bracket & 8mm thick com ply for rear. Side hung shutter in both the panels using 18mm com. ply finished with 1mm thick laminate of approved colour and shade including all ncessary T.W lipping. Brass Butt Hinges, Individual locking arrangement, 100mm long SS brush finish handles, SS Tower Bolt, etc., complete.
| All exposed faces of Steam beech beading polished to the satisfaction of the Architects. The inner side of the Drawer and table finished with 0.8mm Laminate of approved colour and shade. | 8 | Nos
29 | Officer Table without side unit (1350 x 675)
Providing and fixing Officer Table table of size 1350 x 675 X 750mm to detail as shown in drg to shape comprising table top out of 18mm Comply with stiffner of same comply 100 mm wide below the table tob out of 10 x 37 mm Steam Beech moulding to shape along edges.
Table top, sides & Front of drawer finished with 1mm thk laminate of approved colour & shade.
50mm Dia SS Brush Finish wire manager of approved make and quality.
One set of 4 drawers about 450mm wide, 712.5 mm high and 600mm deep to shape supported with 18mm com. ply at front, rear and two sides, 12mm thick com.ply for bottom. Drawer unit of size 75mm at top of the drawer, 2-Nos of 150mm at middle, 262.5mm at bottom, 75mm black skirting at bottom of drawer with necessary TW lipping, telescopic drawer slides,Individual locking arrangement, 100mm long brush finish S.S. handles, etc., complete.
Front face of the drawer finished with 1mm thick laminate of approved colour and shade with necessary steam beech / T.W lipping on the edge of drawers.
| All exposed faces of Steam beech beading polished to the satisfaction of the Architects. The inner side of the Drawer and table finished with 0.8mm Laminate of approved colour and shade. | 1 | Nos
30 | Work Station - Cubicle Table
Providing and fixing Work Station cubical Table of size of 1500 x 1500 x 750mm to detail as shown in drg to shape and comprising table top out of 18 mm. Comply with stiffner of same comply 100 mm wide below the table and 10x 37 mm. Steam Beach moulding to shape along edges.
Table top finished with 1mm thick laminate of approved colour and shade. On front and side of drawer finished with 1mm thick laminate
Keyboard tray made out of 18mm thick Com.Ply finished with 1mm thick laminate of approved colour and shade with necessary Telescopic slides and 2 Nos of 50mm Dia SS Brush Finish wire manager of approved make and quality.
One set of 4 drawers about 450mm wide, 712.5 mm high and 600mm deep to shape supported with 18mm com. ply at front, rear and two sides, 12mm thick com.ply for bottom. Drawer unit of size 75mm at top of the drawer, 2-Nos of 150mm at middle, 262.5mm at bottom, 75mm black skirting at bottom of drawer with necessary TW lipping, telescopic drawer slides,Individual locking arrangement, 100mm long brush finish S.S. handles, etc., complete.
Front face of the storage unit made out of18mm com.ply finished with 1mm thick laminate of approved colour and shade and 18mm com.ply intermediate finished with 1mm thick laminate of approved colour and shadewith necessary Brass Butt Hinges, Locking arrangements, 100mm wide SS Brush finish Handle, Magnetic catch, etc complete
| All exposed faces of Steam beech beading polished to the satisfaction of the Architects. The inner side of the Drawer and table finished with 0.8mm Laminate of approved colour and shade. | 4 | Nos
31 | Discussion Table, DGM Ante Room table (1050mm dia) - Laminate finish
Supplying and instalation of 1050 mm dia Discussion Table, DGM Ante Room table to detail as shown in drg to shape and comprising table top out of 18 mm. Comply with stiffner of same comply 100 mm wide below the table and 10x 37 mm. Steam Beach moulding to shape along edges. table top finished with 1mm thick laminate of approved colour and shade.
| The table supported by 2nos of 475 X 50 mm boxing made out of 18 mm thick com ply finished with 1mm thick laminate of approved colour and shade. | 2 | Nos
32 | Meeting Table (1500mm dia) - Veneer finish
Supply and fixing of 1500 mm dia Meeting Table to detail as shown in drg to shape and comprising table top out of 18 mm. Comply with stiffner of same comply 100 mm wide below the table and 10x 39.5 mm. Steam Beach moulding to shape along edges. table top finished with 3.5mm thick veneer with melamine polish
| The table supported by 2nos of 900 X 50 mm boxing made out of 18 mm thick com ply finished with 3.5mm thick veneer of approved colour and shade with melamine polish | 1 | Nos
33 | Conference Table
Providing and fixing oval shape conference table to detail as per drawing of over all size 8100 x 1200 / 2700 x 750mm high to shape (Make a table of 2 equal parts as shown in drawing) of comprising table top out of 18 mm thick com ply with stiffner of same ply for 100mm wide below the table and 10x 39.5mm steam beech wood moulding to shape finished with melamine polish along edges.
Table top finished with3.5mm thick veneer of approved colour and shade with melamine polish. 18mm thick com.ply vertical support all around the table inside and 16Nos of 18mm thick com ply boxing of sixed 50 x 675mm to shape supports. The vertical inner supports made out of 18mm thick Com.ply boxing and finished with 3.5mm thick veneer with melamine polish.
| All concealed faces of com. ply finished with one coat of wood preservative paint and exposed faces of Steam beech moulding / beading polished to the satisfaction of the Architect / Client. Rate should be inclusive of necessary cutouts for popup box provision, etc complete. Basic cost of veneer should not be less than Rs.865/sqm | 1 | No
34 | Running Table - Laminate finish
Providing and fixing running table with drawer unit to detail as per drg. 600mm wide and 750mm high Continuous table top made out of 18mm comply finished with 1mm thick laminate of approved colour and shade and with10 x 37 mm Steam beech moulding to shape along edges. Table supports at every 1350mm c/c appox,
Keyboard tray made out of 18mm thick Com.Ply finished with 1mm thick laminate of approved colour and shade with necessary telescopic slides and 50mm Dia SS Brush Finish wire manager of approved make and quality.
One set of 4 drawers about 450mm wide, 712.5 mm high and 600mm deep to shape supported with 18mm com. ply at front, rear and two sides, 12mm thick com.ply for bottom. Drawer unit of size 75mm at top of the drawer, 2-Nos of 150mm at middle, 262.5mm at bottom, 75mm black skirting at bottom of drawer with necessary TW lipping, telescopic drawer slides,Individual locking arrangement, 100mm long brush finish S.S. handles, etc., complete.
Front face of the drawer finished with 1mm thick laminate of approved colour and shade with necessary steam beech / T.W lipping on the edge of drawers.
| All concealed faces of comply finished with one coat of wood preservative paint and exposed faces of Steam beech beading polished to the satisfaction of the Architects. The inner side of the Drawer and table finished with 0.8mm Laminate of approved colour and shade. | 106 | Rm.
35 | Running Table - Granite finish
Providing and fixing running table to detail as per drg. 450mm wide Continuous table top made out of 19mm thick BWR ply and top finished with 18mm thick Granite of approved colour and shade with half round nosing edges. 25mm dia ss support to shape at every 1350mm c/c appox,
| All concealed faces of comply finished with one coat of wood preservative paint and exposed faces of Steam beech beading polished to the satisfaction of the Architects. The inner side of the Drawer and table finished with 0.8mm Laminate of approved colour and shade. | 25 | Rm.
36 | Training Room Table (1050 x 450)
Providing and fixing Training Room Table of size 1050 x 450mm x 750mm high table top made out of 18mm comply finished with 1mm thick laminate of approved colour and shade and with10 x 37 mm Steam beech moulding to shape along edges.
| All concealed faces of comply finished with one coat of wood preservative paint and exposed faces of Steam beech beading polished to the satisfaction of the Architects. The inner side of the Drawer and table finished with 0.8mm Laminate of approved colour and shade. | 2 | Nos
37 | Dining Table - Granite top
| Providing & fixing Dining table of size 900 x 900 x 750mm to detail as shown in drg to shape and comprising table top out of 19 mm. BWR ply and top finished with 18mm thick Granite of approved colour and shade with double thick duck nose edge. | 4 | Nos
38 | Reception Table - Corian top
Providing and fixing Receptional table of size 1800 x 750X750/1050mm to detail as shown in drg.
Table top, front, sides and 75mm thick corner ply boxing made out of 18mm comply finished with 6mm thick corian / Asian top with pattern of approved colour and shade with edge nosing. Front and side of drawer should be finished with 1mm thk laminate of Approved colour and shade .,
50mm dia SS Brush Finish wire manager of approved quality .
One set of 4 drawers about 450mm wide, 712.5 mm high and 600mm deep to shape supported with 18mm com. ply at front, rear and two sides, 12mm thick com.ply for bottom. Drawer unit of size 75mm at top of the drawer, 2-Nos of 150mm at middle, 262.5mm at bottom, 75mm black skirting at bottom of drawer with necessary TW lipping, telescopic drawer slides,Individual locking arrangement, 100mm long brush finish S.S. handles, etc., complete.
Front face of the drawer finished with 1mm thick laminate of approved shade and colour with TW lipping on the edge of drawer.
| All concealed faces of comply finished with one coat of wood preservative paint and exposed faces of Steam beech beading polished to the satisfaction of the Architects / Client. The inner side of the Drawer and table finished with 0.8mm Laminateof approved colour and shade. Basic Cost of Corian / Asian should not be less than Rs.8750/sqm | 1 | No
39 | Reception Table - Laminate finish- writing ledg, glass top ss ledge
Providing and fixing Reception Table table of size 1200 x 600 X 750 / 1050mm to detail as shown in drg to shape comprising table top out of 18mm Comply with stiffner of same comply 100 mm wide below the table tob out of 10 x 37 mm Steam Beech moulding to shape along edges.
Table top, sides & Front of drawer finished with 1mm thk laminate of approved colour & shade.
Provide 150mm wide 12mm thick toughened glass with SS supports in top of the table at 1050mm level.
1 Pencil drawers about 375mm wide,75 mm high and 550mm deep to shape supported with 18mm com. ply at front, rear and two sides, 12mm thick com.ply for bottom with necessary TW lipping, telescopic drawer slides,Individual locking arrangement, 100mm long brush finish S.S. handles, etc., complete.
| All exposed faces of Steam beech beading polished to the satisfaction of the Architects. The inner side of the Drawer and table finished with 0.8mm Laminate of approved colour and shade. | 1 | No
V | STORAGES/ SIDE UNITS
40 | Low Level Storage - Veneer finish
Providing and fixing low level storage to detail of drawing 450mm wide and 750mm high comprising.
18 mm thick comply fixed at top, sides, vertical and bottom at 75mm and one intermediate shelf with necessary S.S bracket and 8mm thick com ply for rear, 10x39.5mm steam beech moulding along the edges and finished with Melamine polish
Side hung shutters in required leaves with 18 mm thick comply finished with 3.5mm veneer melamine polish of approved colour and shade, including necessary grooves, Brass Butt Hinges, Individual locking arrangements, 100mm long S.S brush finish handles, Brass Tower Bolt ,Magnertic lock etc. complete.
| All concealed faces of comply finished with one coat of wood preservative paint and exposed faces of Steam beech beading polished to the satisfaction of the Architects / Client. The inner side of the storage finished with 0.8mm thick laminate. Basic cost of veneer should not be less than Rs.865/sqm | 9 | sqm
41 | Low Level Storage - laminate Finish
Providing and fixing low level storage to detail of drawing 450mm wide and 750mm high comprising.
Storage top made out of 18mm thick com.ply with Steam beech moulding 10 x 37 mm Steam beech moulding to shape along edges, 18 mm thick comply fixed at sides, verticals and bottom at 75mm and one intermediate with necessary S.S bracket and 8mm thick com ply for rear
Side hung shutters in required leaves with 18 mm thick comply finished with 1mm thick laminate of approved colour and shade including all ncessary T.W lipping, necessary box type Hinges, Individual locking arrangements, 100mm long S.S brush finish handles, Brass Tower Bolt, Magnetic lock, etc. complete.
| All exposed faces of Steam beech beading polished to the satisfaction of the Client / Architects. The inner side of the storage finished with 0.8mm thick laminate of approved colour and shade. | 43 | sqm
42 | Low Level Storage - Granite top
Providing and fixing low level storage to detail of drawing 450mm wide and 750mm high comprising.
Storage top made out of 18mm thick com.ply finished with 18mm thick Granite of Approved colour with half round nosing edges, 18 mm thick comply fixed at sides, verticals and bottom at 75mm and one intermediate with necessary S.S bracket and 8mm thick com ply for rear
Side hung shutters in required leaves with 18 mm thick comply finished with 1mm thick laminate of approved colour and shade including all ncessary T.W lipping, necessary box type Hinges, Individual locking arrangements, 100mm long S.S brush finish handles, Brass Tower Bolt, Magnetic lock, etc. complete.
| All exposed faces of Steam beech beading polished to the satisfaction of the Client / Architects. The inner side of the storage finished with 0.8mm thick laminate of approved colour and shade. | 8 | sqm
43 | Medium Height Storage - Laminate finish
Providing and fixing Medium height storage unit with shutter of size 1200 mm high and 450 mm deep to detail comprising storage top out of 18mm thick com ply with 10 x 37 mm Steam beech moulding to shape along edges, 18mm thick com ply for top, sides, Two intermediates and bottom at 75mm level. Storage back 18mm thick com ply for side hung shutters with half round nosing laminated edge finish of required leaves with necessary, TW lipping, box type Hinges, SS Tower Bolts, Individual locking arrangements, ball magnetic catch, 150mm long SS Brush Finish handle etc., complete
| All exposed faces of Steam beach beading polished to the satisfaction of the Architects. The inner side of the storage finished with 0.8mm thick Laminate of approved colour and shade. | 38 | sqm
44 | Open Storage with Glass shelf - Laminate finish
Providing and fixing Open Storage with Glass shelf to detail of drawing 450mm wide and 1200mm high comprising.
| 18 mm thick comply fixed at sides, top and bottom finished with 1mm thick laminate of approved colour and shad and Three intermediate using 12mm thick clear float glass with necessary S.S bracket .Measurement shall be consider as flat size of open storage only. | 29 | sqm
45 | Open Storage with Glass shelf - Venner finish
Providing and fixing Open Storage with Glass shelf to detail of drawing 450mm wide and 1200mm high comprising.
| 18 mm thick comply fixed at sides, top and bottom finished with 3.5mm veneer with melamine polish of approved colour and shade and Three intermediate using 12mm thick clear float glass with necessary S.S bracket .Measurement shall be consider as flat size of open storage only. | 7 | sqm
46 | Over Head Storage - Laminate finish
Providing and fixingOver Head Storage - Laminate finish to detail of drawing 450mm wide and 600mm high comprising.
Storage top made out of 18mm thick com.ply with Steam beech moulding 10 x 37 mm Steam beech moulding to shape along edges, 18 mm thick comply fixed at sides, verticals and bottom at 75mm and one intermediate with necessary S.S bracket and 8mm thick com ply for rear
Side hung shutters in required leaves with 18 mm thick comply finished with 1mm thick laminate of approved colour and shade including all ncessary T.W lipping, necessary box type Hinges, Individual locking arrangements, 100mm long S.S brush finish handles, Brass Tower Bolt, Magnetic lock, etc. complete.
| All exposed faces of Steam beech beading polished to the satisfaction of the Client / Architects. The inner side of the storage finished with 0.8mm thick laminate of approved colour and shade. | 4 | sqm
VI | Miscellaneous
47 | Wall Panelling - Veneer Finish
| Providing and fixing panelling on wall. Framing shall consist of size 50 x 25 x 2mm thick (0.791 kg/m) Aluminium box Section at 600mm c/c. both ways horizontally and vertically on the wall. The frame work should be covered by 8mm thick com. ply and finished with 3.5mm thick veneer with necessary grooves and finished with melamine polish of approved colour and shade. All concealed faces of comply painted with one coat of wood preservative paint before fixing. Basic cost of veneer should not be less than Rs.865/sqm | 109 | sqm
48 | Wall panelling with frame - laminate Finish
| Providing and fixing laminate panelling on wall. Framing shall consist of size 50 x 25 x 2mm thick (0.791 kg/m) Aluminium box Section at 600mm c/c. both ways horizontally and vertically on the wall. The frame work should be covered by 8mm thick com. ply and finished with 1mm thick laminate of approved colour and shade. All concealed faces of comply painted with one coat of wood preservative paint before fixing. | 54 | sqm
49 | Wall panelling without frame- laminate Finish
| Providing and fixing laminate panelling on wall. 18mm thick com. Ply finished with 1mm thick laminate of approved colour and shade with stiffner. All concealed faces of comply painted with one coat of wood preservative paint before fixing. | 96 | sqm
50 | Wall panelling - without Finish
| Providing and fixing panelling on wall in conference room. 18mm thick com. ply panelling from floor level to False ceiling level with necessary stiffner wherever required. All concealed faces of comply painted with one coat of wood preservative paint before fixing. | 143 | sqm
51 | Acoustical Wall Panelling:
| Providing and fixing of Armstrong or approved equivalent ‘Optra Acoustical Wall Panelling’ with square edges made of fibre glass substrate 15mm thick and wrapped on the front side with an acoustically transparent and fire-resistant fabric with an option of colours as per the choice of the Architect/ client of size 600 x 1200 or 600x600 mm to be affixed to wall using Wall panel impalers supplied by M/s Armstrong Industries India Pvt. Ltd and construction adhesives as per the instructions laid down by the manufacturer. | 243 | sqm
52 | ACP covering with CNC Cutting
| Providing and fixing ply covering to detail, 18mm thick com ply stiffner on horizontal and verticals at 600mm c/c on both ways fixed to wall with necessary screws, aluminium cleats, rawl plugs, etc., complete. finished with 3mm thick ACP CNC cutting design of approved colour and shade. All concealed faces of com ply painted with one coat of wood preservation paint before fixing etc., complete. Basic cost of ACP should not be less than Rs.1100 per Sqm | 5 | sqm
53 | Column Cladding
| Providing and fixing cladding around the columns to detail as per drawing . comprising 18mm thick com. ply stiffner on both ways of required nos, covered with 18mm com ply and finished with 1 mm thick laminate of approved colour and shade. | 23 | sqm
54 | Wooden Bamboo Blinds
| Providing and fixing e Vista or equivalent make wooden Bamboo blinds of Approved design and shade. Basic cost of blinds should not be less than Rs.1400 per Sqm | 17 | sqm
Note: Measurment for the Blinds area shall be considered for the opening size of windows only.
55 | Roller Blinds
| Providing and fixing of Vista or Equivalent make of blinds with Approved design and shade. Basic cost of blinds should not be less than Rs.1200 per Sqm | 134 | sqm
Note: measurement of blinds area shall be considered the opening size of windows only
56 | Ply Boxing
| Providing and fixing 18mm thk Com.Ply covering with same Com.ply stiffner on horizontal and verticals at required distance fixed to wall with necessary screws, aluminium cleats, rawl plugs, etc., complete. 18mm Com.ply finished with 1mm laminate of approved colour and shade with necessary grooves and beading. | 70 | Sqm
57 | CNC cutting board
| Providing and fixing CNC Cutting MDF of 18mm thickness trellies work and finished with Duco Paint. All concealed faces of com.ply painted with one coat of wood preservation paint before fixing. | 7 | Sqm
58 | Calcium silicate Board Covering
| Providing and fixing 12mm thick Calcium silicate Board covering with necessary Aluminium box section etc complete and finished neatly. Rate Should be inclusive of two coats of emulsion paint of approved colour and shade including one coat of primer. | 5 | Sqm
59 | BWR ply Shutters -Laminate Finish
Providing and fixing 19mm thk. BWR ply shutters with same ply frame
Side hung shutters in required leaves with 19mm thick BWR ply and finishd with 1mm thick laminate of Approved colour and shade on both sides of the shutters. One intermediate 19mm thick BWR ply shelf with necessary support and finished with 0.8mm thick laminate of approved colour and shade.
| Rate should be inclusive of all necessary fittings like Brass Butt Hinges, ball catch, 100mm long S.S. Brush finish handle, Brass Tower Bolt etc, complete. | 7 | sqm
60 | Corian Top cladding
| Supplying and fixing 12mm thick Acrylic Surface Tops (Corian) with edge nosing cladding with necessary fixing materials etc complete. | 2 | Sqm
61 | Toughened Glass cladding / writing board with ss stud
| Supplying and fixing 8mm thick approved make Toughened Glass cladding / writing board with ss stud | 11 | Sqm
62 | Wall Paper
| Supplying and fixing Wall Paper of approved colour and design with necessary adhesive, etc. complete. Basic cost of Wall Paper is Rs.1,500 per Sqm | 32 | Sqm
63 | Trap Door
| Providing and fixing trap door of size about 2000 x 1000mm for AC indoor unit to detail, 40 x 30mm second class T.W frame with 12mm thk BWR ply shutter and finished with 1mm thk bright white colour laminate including necessary hardware fitting like tower bolt, ball catch and chain hang from roof slab etc, complete. | 4 | Nos
64 | Carpet Flooring
| Providing and fixing Fire Redardent Carpet Flooring of nominal thickness of 6mm approved colour & design | 226 | Sqm
65 | Laminated wooden flooring
| Providing & fixing 12mm thick Laminated wooden flooring (AC4) with edge nosing and necessary end locking arrangements. Rate should be inclussive of steps riser and thread on both sides | 17 | sqm
66 | S.S Sink
| Nirali make or equivalent S. S. sink (single bowl) with necessary CP brass waste fittings, 32mm CP brass, and bottle trap with extension piece etc. complete.Rate shall also include one C P SWAN NECK TAP with swinging casted spout. | 2 | No
67 | Signage Board-Cabin & Toilet (150 x 150mm)
| Supply & fixing of signage Board for Cabin & Toilet of size 150 x 150mm finished with SS brush finish and necessary engraving | 40 | Nos
68 | Pull & Push signage board (100 x 100mm)
| Supply & fixing of Pull & Push signage board of size 100 x 100mm finished with with SS brush finish with necessary engraving | 34 | sets
69 | ACP Name Board (4' x 4') with CNC cutting
| ACP Name Board (4' x 4') with CNC cutting design covering with 4mm thick acralic sheet fixing over the 18mm ply boxing as shown in drawing | 2 | Sqm
70 | Enamel Paint
| Prepare surface and applying two coats of Synthetic Enamel paint of approved colour and shade over a coat of anti corresive paint . | 25 | sqm
71 | Interior Emulsion Paint
| Prepare surface and paint two coats of Plastic emulsion paint of approved colour and shade over a coat of primer including Alteck putty after thoroughly scrapping the existing internal walls. | 250 | sqm
I | SANITARY FIXTURES
1 | European Water Closet
| Supplying and fixing approved make group one colour wall hung cascade European Water Closet (EWC) with flush tank fixing in wall dado using suitable fixing materials like brass screws T.W. plugs etc. (Parryware - cascade NXT, Hindware -20028) | 1 | Nos
2 | Ordinary Wash Basin
| Supplying and fixing approved make wash basin of size 550x400mm with 32mm CP waste fittings and CP bottle trap and with extension piece fitted with a pair of CI brackets complete with all fixing materials such as brass screws and T.W. plugs etc. Parryware - Indus - 550 x 450 | 1 | Nos
3 | Oval Wash Basin
| Supplying and fixing lavatory suite comprising group one colour oval wash basin of size 550x400mm with 32mm CP waste fittings and CP bottle trap and with extension piece, 1 no. 15mm CP angle valve fitted with a pair of CI brackets, complete with all fixing materials such as brass screws and T.W. plugs etc. (Parryware- Cascade NXT, Hindware-Zen 560 x 450 ) | 2 | Nos
4 | Mirror with Frame
| Supplying and fixing 6mm thick approved make clear mirror made out of 35mmX20mm steam beach wood frame finished with melamine polish and 12mm thick BWR plywood back and finished neatly.Rate should be inclusive of all necessary fixtures and fittings. | 1 | Sqm
5 | Towel Rod
| Supplying and fixing chromium plated towel rod of approved make 20mm dia, 600mm long with chromium plated concealed brackets fixing to wall dado using suitable size non-corrosive screws, teak wood plugs etc. complete. (Jaguar - No. 1111N) | 1 | Nos
6 | Coat Hooks
| Supplying and fixing approved make chromium plated coat hooks with twin arms, heavy quality fixing to rear of wooden shutter of toilet doors with CP screws etc, complete. | 1 | Nos
PART II - SOIL, WASTE AND VENT PIPE LINES
1 | PVC Pipe for waste Lines
Supplying and fixing approved make PVC pipes and specials equivalent make including cutting pipes, fixing to walls or brackets using MS clamps, making joints using solvent cement solution, using ring seal couplers on size of pipes of fully sizes cutting walls or concrete surface, making grooves in masonry to conceal the pipes, restoring damaged portions with CM 1:4 and jelly, to their original condition, conducting leak test, fixing and removing temporary scaffolding, MS frame work & clamp for pipe laying, conveying dismantled debris and disposal of debris away from the size etc. complete.Finolex, Prince, Truebore
a | 40mm dia. 6kg class pipes. | 5 | Rmt
b. | 63mm dia. 6kg class pipes. | 5 | Rmt
c. | 75mm dia. 6kg class pipes. | 5 | Rmt
d. | 110mm dia. 6kg class pipes. | 5 | Rmt
2 | Floor Traps
| Supplying and laying custom built (prefabricated) PVC floor sumps / floor traps fabricated out of 110mm dia 6kg Class PVC pipes with inlet and outlets from 40mm upto 75mm, including providing water seal, fixing to a perfect level, laying cement concrete in 1:3:6 mix using 20mm size coarse graded aggregate, providing 150x150mm size C.P / PVC Symet colour grating with frame alround, at 4mm below finished floor level making holes in masonry or concrete cutting surfaces, conveying all dismantled portions and clearing the site, making leak proof joints and testing etc., complete and as directed. | 1 | Nos
PART III - WATER SUPPLY
1 | PVC Pipe lines for Water Supply
Supplying and fixing approved make UPVC pipe with ISI brand fittings such as tees, elbows, unions, nipples, flanges, etc. including cutting, threading, cutting chassing in walls and concealing the pipes in wall wherever laid inside the toilet complete with making holes in walls, floors, slabs, etc. earthwork excavation, back filling to consolidation, redoing the distrubed portions,MS frame work & clamp for pipe laying, MS/brick in CM supports testing and commissioing complete as directed.Finolex, Prince, Truebore
a. | 15mm dia UPVC pipe | 5 | Rmt
b | 25mm dia Upvc pipe | 10 | Rmt
c | 32mm dia UPVC pipe | 5 | Rmt
2 | Angle Valve
| Supplying and fixing 15mm CP inlet valve with CP connection (Jaguar :No. 059) | 2 | Nos
3 | Two Way Bib Cock
| Supplying and fixing 15mm CP two way bib cock. (Jaguar No. 041) | 1 | Nos
4 | Bib Cock (long body)
| Supplying and fixing 15mm CP bib cock longbody. (Jaguar :No. 123 or No:127) | 2 | Nos
5 | Jet Spray
| Supplying and fixing metal hose Jet spray (Jaguar No:573) | 1 | Nos
Total

## e
SBI LIFE INSURANCE CO LTD
PROPOSED INTERIOR WORKS FOR SBI LIFE, REGIONAL OFFICE AT KODAMBAKKAM, CHENNAI
BILL OF QUANTITIES - ELECTRICAL WORKS
Sl. No | Description | Qty | Unit | Rate | Amount
1 | Switch Boards
1.1 | UPS Panel
Design, Manufacture, Transport, Supply, Erection with necessary metal base frames, Earthing, Testing and Commissioning of the following UPS Panels, free standing dust and vermin proof by construction of 14 SWG CRCA sheets with bolted construction powder coated panel incoming and outgoing breaker details as per the technical specification, SLD & as mentioned below.
Technical specification and Bill of Materials for UPS panel.
Floor mounting free standing cubicle type control panel shall consist of the following
Main busbar- TR - 100A TP+2N AL. 25kA Busbar(1R -25 x 6mm Al. per ph, 1R- 25 x 6mm per Neutral)
Earth busbar - 2R 25x3mm Cu. Flat
INCOMING:
2 Nos –63A 25KA TP+2N MCB
2 Sets - LED type RYB indication lamps with control fuses.
1 Set - Analog Voltmeter, Ammeter & KWH Meter.
1 Set – Control terminal units control fuses
OUTGOINGS
4 Nos - 32A TP+2N 25kA MCB
BUSBAR RATING:
One set: 100A TPN 25KA for 1 sec. Al. bus bars with colour coated heat shrinkable PVC sleeves with DMC/SMC bus bar supports and suitable earth bus.
PH:1R 25 x 6mm Al.Flat
N:2R 25 x 6mm Al.Flat
E:2R 25 x 3mm Cu.Flat
CABLE GLAND PLATES : 3mm thick
| CABLE ENTRY & EXIT : TOP/BOTTOM | 1 | Sets
2 | Distribution Boards
2.1 | LDB 1 & 2
Supply, erection, earthing, testing and commissioning of the following MCB DB's IP 42 Protection Metal double Door powder coated including all interconnections and accessories like bolts, nuts and associated civil works. MCB DBs shall have comprising as follows. The same shall be concealed to the wall. (4-way TPN 7Seg. MCB DB)
1 no incomer feeder fitted with 32 A TPN MCB
3 nos of 25A DP 30mA RCCBs as outgoing feeders
11 nos of 6A SP MCBs as outgoing feeders
| 1 no of 16A SP MCBs as outgoing feeders | 2 | Nos
2.2 | PDB - 1 & 2
Supply, erection, earthing, testing and commissioning of the following MCB DB's IP 42 Protection Metal double Door powder coated including all interconnections and accessories like bolts, nuts and associated civil works. MCB DBs shall have comprising as follows. The same shall be concealed to the wall. (4-way TPN 7Seg. MCB DB)
1 no incomer feeder fitted with 32 A 4-pole MCB
3 nos of 25A DP 100mA RCCBs as outgoing feeders
6 nos of 10 A SP MCBs as outgoing feeders
| 6 nos of 16 A SP MCBs as outgoing feeders | 2 | Nos
2.3 | Timer for display board
| 1 no 0-24 hr electronic timer along with 1 no 12A 2-pole air break contactor enclosed in a powder coated MS box fabricated out of 16 Swg CRCA with a screwed front cover plate and mounted on wall. The same shall be completely wired. | 1 | No
2.4 | UDB - 1 & 2
Supply, erection, earthing, testing and commissioning of the following MCB DB's IP 42 Protection Metal double Door powder coated including all interconnections and accessories like bolts, nuts and associated civil works. MCB DBs shall have comprising as follows. The same shall be concealed to the wall. (6-way TPN 7Seg. MCB DB)
1 no incomer feeder fitted with 32 A TP+2N MCB
3 nos of 25A DP MCBs as outgoing feeders
16 nos of 10 A SP MCBs as outgoing feeders
| 2 nos of 16 A SP MCBs as outgoing feeders | 2 | Nos
2.5 | UPS DB - 3 for Server.
Supply, erection, earthing, testing and commissioning of the following MCB DB's IP 42 Protection Metal double Door powder coated including all interconnections and accessories like bolts, nuts and associated civil works. MCB DBs shall have comprising as follows. The same shall be concealed to the wall. (6-way SPN MCB DB) ( UPS DB-1 )
1 no 32 A DP MCB as incomer
2 nos 10A SP MCBs as outgoing feeders.
| 2 nos 6/16A SP MCBs as outgoing feeders. All the blank spaces shall be provided with dummy plates as required. | 1 | Nos
2.6 | ELDB -1 & 2
8W SPN MCB DB with 'C' curve MCB's
Incoming:
1 No - 25A DP 30mA RCCB
Outgoing:
| 6 Nos - 6/10A SP MCB | 1 | Nos
3 | INVERTER / MCCBs / MCBs / ISOLATORs / STARTERs etc.
a | MCCBs for UPS ISOLATION Control
| Supply and installation of 63A 4-pole MCB 10 ka, D-curve housed in powder coated MS box to be fixed on wall for controlling UPS units | 2 | Nos
b | MCBs for A/C Control
| Supply and installation of 40A 4-pole MCB , 10 ka, C-curve housed in powder coated MS box to be fixed on wall for controlling compressor units | 1 | Nos
c | Supply and installation of 32A DP COS with powder coated MS enclosure to be fixed to the wall with suitable angle iron frame. | 1 | No
d | Supply,Installaion,Testing and Commissioning of 1KVA ON LINE INVERTER of Single phase input ,single phase output and with 30min SMF Battery Backup for Emergency lighting. | 1 | No
4 | Wiring of light, fan, 6A sockets and exhaust fan points
Wiring for light points with 2 runs of 1.5 Sqmm 1.1kV grade 1.1kV grade FRLS, single core, multistrand copper wire ( For phase and neutral ) with one run of 1.1kV grade 1.1kV grade FRLS 1.5 Sqmm PVC insulated, single core, stranded, copper wire for earthing ( green colour ) in 20mm dia MS conduit, 16 Swg thick ( ISI marked ) with necessary accessories including supplying and fixing 6A single pole modular switch housed in manufacturers zinc passivated MS box with cover plate.
4.1 | 1 light controlled by 1 switch | 40 | Nos
4.2 | 2 lights controlled by 1 switch | 70 | Nos
4.3 | 3 lights controlled by 1 switch | 18 | Nos
4.4 | 4 lights controlled by 1 switch | 16 | Nos
4.5 | 5 lights controlled by 1 switch | 6 | Nos
4.6 | Exhaust fan point | 5 | Nos
4.7 | Ceiling fan point with step type electronic regulator and anchor fan hook | 2 | No
4.8 | Supply and laying of 3 R 2.5 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in 20mm dia MS conduit, 16 Swg thick ( ISI marked ) concealed in wall by chase cutting for circuit mains from LDBs to switch boxes | 1000 | Mts
4.9 | Supply, wiring, testing and commissioning of 3R 2.5sqmm PVC insulated 1.1kV grade FRLS multistrand copper wire in 20mm dia 2mm thick MS conduit with all accessories as required as per site conditions. (Emergency lighting circuits). | 300 | Mts
4.1 | Supply and laying of 3 R 2.5 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in 20mm dia MS conduit, 16 Swg thick ( ISI marked ) concealed in wall by chase cutting for name boad lighting to be connected to LDB through a timer | 50 | Mts
5 | Wiring for UPS sockets
5.1 | Supply and laying of 3 R 2.5 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in 20mm dia MS conduit, 16 Swg thick ( ISI marked ) concealed in wall by chase cutting and laying through partitions for UPS power sockets complete with all accessories ( set of 4 nos workstation sockets to be connected to one circuit ) | 1400 | Mts
5.2 | Supply and laying of 3 R 2.5 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in existing racewace / conduit, concealed in wall by chase cutting and laying through partitions for UPS power sockets complete with all accessories ( set of 4 nos workstation sockets to be connected to one circuit ) | 600 | Mts
5.3 | Supply and installation of 3 nos 6A multi pin sockets housed in a single manufacturers zinc passivated MS box with cover plates. The boxes to be fixed either in wall or partitions/ work stations. | 143 | Nos
5.4 | Supply and laying of 3 R 4 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in 20mm dia MS conduit, 16 Swg thick ( ISI marked ) concealed in wall by chase cutting and laying through partitions for UPS power sockets complete with all accessories ( set of 2 nos 16A sockets to be connected to one circuit ) | 100 | Mts
5.5 | Supply and installation of 6/16A modular type multi pin switched socket housed in manufacturers zinc passivated MS box to be concealed on the wall ( For UPS power ) | 2 | Nos
5.6 | Supply and installation of 1 nos 6A multi pin socket Controled by 1 no 6A switch modular type housed in a single manufacturers zinc passivated MS box with cover plates. The boxes to be fixed either in wall or partitions. (RUU Cabin work stations). | 12 | Nos
5.7 | Supply and installation of 16A modular type Master Control Switch housed in manufacturers zinc passivated MS box to be concealed on the wall ( For UPS power ). | 143 | Nos
6 | RACE WAYS, FLOOR JUNCTION BOXES & PVC CONDUITS
6.1 | Supply and running of extruded corrosion proof box type Aluminium Raceways of size 100 x 38 x 1.6mm with smooth edges and free from any electromagnetic interference or data loss along with 1 Run 14 SWG cu. wire required as per the site condition. The rate shall also include necessary floor chipping, wall chasing work. ("MK" Make or equivalent ) | 100 | Mtrs
6.2 | Supply and Installation of high quality M.S Powder coated under floor junction box with S.S. plate covers with s.s.screws of the following sizes. The junction box shall be earthed with 2.5sqmm copper wire with all hardwires and accessories as required including all clamps and hardwires for fixing the same. ("MK" make or Equivalent)
a | 150 x 150 x 60 -75mm for UPS & Data, Voice ( Type - JB 150) | 35 | Nos
b | 250 X 250 x 60-75mm 3-compartments junction box | 10 | Nos
c | 250 x 200 x 50mm -2 Compartment (Type EVB 250/2) Vertical Access Box | 10 | Nos
d | Supply and running of 32mm dia 1.8mm thick PVC conduit embedded in floor / wall for running the data / voice / UPS power cables. The rate shall also include necessary floor chipping, wall chasing work. | 60 | Mtrs
e | Supply and running of 25mm dia 1.8mm thick PVC conduit embedded in floor / wall for running the data / voice / UPS power cables. The rate shall also include necessary floor chipping, wall chasing work. | 120 | Mtrs
7 | Raw power socket wiring
7.1 | Supply and laying of 3 R 2.5 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in 20mm dia MS conduit, 16 Swg thick ( ISI marked ) concealed in wall by chase cutting and laying through partitions for Raw power sockets complete with all accessories ( set of 6 nos workstation power sockets to be connected to one circuit )- For work stations. | 1000 | Mts
7.2 | Supply and laying of 3 R 2.5 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in existing racewace / conduit, concealed in wall by chase cutting and laying through partitions for UPS power sockets complete with all accessories ( set of 6 nos workstation sockets to be connected to one circuit ) | 200 | Mts
7.3 | Supply and installation of 2 nos 6A multi pin socket Controled by 1 no 10A switch modular type housed in a single manufacturers zinc passivated MS box with cover plates. The boxes to be fixed either in wall or partitions/ work stations. | 25 | Nos
7.4 | Supply and installation of 1 nos 6A multi pin socket Controled by 1 no 6A switch modular type housed in a single manufacturers zinc passivated MS box with cover plates. The boxes to be fixed either in wall or partitions. (Workstations). | 118 | Nos
7.5 | Supply and installation of 1 nos 6A multi pin socket Controled by 1 no 6A switch modular type housed in a single manufacturers zinc passivated MS box with cover plates. The boxes to be fixed either in wall or partitions. (excluding the work stations). | 23 | Nos
7.6 | Supply and laying of 3 R 4 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in 20mm dia MS conduit, 16 Swg thick ( ISI marked ) concealed in wall by chase cutting and laying through partitions for Raw power sockets complete with all accessories ( set of 2 nos 16A sockets to be connected to one circuit ) | 400 | Mts
7.7 | Supply and laying of 3 R 4 Sqmm 1.1kV grade FRLS stranded copper wire ( one for earth, green colour ) in Existing Raceways / conduit, conceiled in wall by chase cutting and laying through partitions for Raw power sockets complete with all accessories ( set of 2 nos 16A sockets to be connected to one circuit ) | 150 | Mts
7.8 | Supply and installation of 6/16A modular type multi pin switched socket housed in manufacturers zinc passivated MS box to be concealed on the wall ( For Raw power ) | 30 | Nos
8 | TV connectivity
8.1 | Supply and installation of 25 mm dia PVC conduit, ISI marked medium grade to be laid on wall, and partitions from main Hub and main tel junction to all work stations as marked in the drawing. | 500 | Mts
8.2 | Supply and installation of 20 mm dia PVC conduit, ISI marked medium grade to be laid on wall, and partitions from main Hub and main tel junction to all work stations as marked in the drawing. | 250 | Mts
8.3 | Supply, Installation, testing and commissioning of TV Coaxial socket outlet ,moulded front plate GI anodized enclosure in the wall and other associated accessories including chasing embedding rough plastering as required as per the site conditions | 3 | Nos
8.4 | TV Coaxial cable | 120 | Mtrs
9 | Light fittings and fans
9.1 | Installation including assembling, testing and commissioning of 600x600mm modular recess mounted fitting with 36 W LED lamps and sutable drivers and suspended from ceiling either with 20mm dia 16 Swg thick MS conduit ( ISI marked ) down rods( 0.8mt long approx: ) and heavy duty ball and sockets, sealing plate, check nuts etc or with 8 Swg GI chain and giving connections | 51 | Nos
9.2 | Installation including assembling, testing and commissioning of surface mounted 5W LED cove light fitting with Drivers. | 20 | Nos
9.3 | Installation including assembling, testing and commissioning of recess mounted down light fitting with 15 W LED lamps and sutable drivers. | 223 | Nos
9.4 | Installation including assembling, testing and commissioning of Surface mounted down light fitting with 15 W LED lamps and sutable drivers. | 6 | Nos
9.5 | Installation including assembling, testing and commissioning of Wall mounted down light fitting with 9W or 10W LED lamps and sutable drivers for Mirror light fitting. | 5 | Nos
9.6 | Installation including assembling, testing and commissioning of LED Batten with 20W Tube with system efficacy of 100Lm/W , delivering 1800Lumens. | 2 | Nos
10 | Supply and installation of exhaust fans & Ceiling fans
10.1 | Supply and installation of 300mm dia low duty exhaust fan with auto gravity louvre | 4 | Nos
10.2 | Supply and installation of 1200mm dia sweep type ceiling fan. | 2 | No
11 | UPS wiring
11.1 | Supply, Laying, testing and commissioning of 4R 1CX25Sqmm flexible cables in flexible hose. (From UPS Isolation Box to UPS 1 & 2) | 20 | Mts
11.2 | Supply, Laying, testing and commissioning of 5R 1CX25Sqmm flexible cables in flexible hose. (From UPS 1 & 2 to UPS O/P Panel) | 30 | Mts
11.3 | Supply, Laying, testing and commissioning of 4R 16 Sqmm 1.1kV grade FRLS multi stranded copper wire in 32mm dia 16 Swg thick MS conduit ( ISI marked ) including terminations with 6 Sqmm copper crimping sockets. (From UPS O/P Panel to UPS DB 1 & 2) | 80 | Mts
11.4 | Supply and installation of 3R 6 Sqmm 1.1kV grade FRLS multi stranded copper wire in 32 mm dia GI flexible conduit. (From UPS O/P Panel to Server DB) | 25 | Mts
12 | Power wiring
12.1 | Supply, installation, testing and commissioining of 3R 4 Sqmm 1.1kV grade FRLS multistranded copper wire in 25mm dia 16 Swg thick MS conduit ( ISI marked ) from DB 1 to 20 A A/C sockets | 90 | Mts
12.2 | Supply and installation of 20A 3-pin metal clad socket housed in powder coated MS box with 3-pin metal clad plug and 20A DP MCB, 10 ka housed in powder coated MS box to be fixed on wall at different locations for controlling split A/C units. (for server room). | 2 | Nos
13 | UG cable
13.1 | Same as item no 13.1, but 4Cx25 Sqmm XLPE Al. + 2nos 10 swg cu wire | 50 | Mts
13.2 | Same as item no 13.1, but 4Cx10 Sqmm copper + 2nos 10 swg cu wire ( For PDB) | 100 | Mts
13.3 | Same as item no 13.1, but 4Cx6 Sqmm copper + 2nos 10 swg cu wire ( For LDB) | 100 | Mts
Terminations of following cable with SIBG glands and copper crimping sockets and earthing of glands with copper clip and connecting the same to earth grid with 14 Swg copper wire
13.4 | 4x25 Sqmm | 4 | Nos
13.5 | 4x10 Sqmm | 4 | Nos
13.6 | 4x6 Sqmm | 4 | Nos
14 | Earthing
14.1 | Supply, installation, testing and commissioing of 600x600x3mm copper plate electrode complete with 25mm dia GI watering pipe as per IS-3043 complete with all accessories like watering funnel, clamps etc.The same to be installed in a pit 3 Mt deep and filled with alternate layers of charcoal, salt mixed with river sand. A brick work masonary shall be constructed of size 600x600x150mm and cement plasted at both inside and outside walls. A 3mm thick cast iron plate with frame work shall be placed over the chamber ( For UPS units ) | 4 | Nos
14.2 | Supply and installation of 25x3 mm copper strip to interconnect the earth pits with SSB and other equipments | 100 | Mts
14.3 | 8 SWG Cu. Wire for DBs earthing | 200 | Mts
14.4 | 10 SWG Cu. Wire for Gland earthing | 50 | Mts
14.5 | Supply and installation of 10 Sqmm multi strand copper wire 1.1kV grade FRLS insulated to be drawn in 25mm dia PVC conduit 2mm thick and to be clamped partially on wall with GI clamps and partially burried in ground and terminations at both ends with copper crimping sockets ( For UPS earthing ) | 80 | Mts
14.6 | MS ITEMS
| Supply, Fabrication and Erection of M.S. Material for ladder type cable trays, cable supports, SB, DB's supports, iron embedded in the wall, steel structure in open area painted with two coats of primer and two coats of enamel paint. | 100 | Kgs
15 | Public address system wiring
15.1 | Supply and installation of 2 core 24/0.2mm dia twin twisted copper conductor PVC insulated cable drawn in 20mm dia medium grade PVC conduit ( ISI marked ) including clamping the same with GI clamps on ceiling, wall, through partitions etc and chase cutting of wall wherever required | 200 | Mts
15.2 | Supply and installation of 6W ceiling mounted ring speaker in plastic mould with built in transformer | 35 | Nos
15.3 | Supply and installation of volume control housed in GI box | 28 | Nos
Total value of Electrical works

## l
SBI LIFE INSURANCE CO LTD
PROPOSED INTERIOR WORKS FOR SBI LIFE, REGIONAL OFFICE AT KODAMBAKKAM, CHENNAI
BILL OF QUANTITIES - LIGHT FIXTURES
Sl. No | Description | Qty | Unit | Rate | Amount
1 | Supply of 600x600mm modular recess mounted fitting with 36W LED lamps and driver. (Cat Ref. No. - CROMPTON LCTLRN36FOCDL) or Approved Equivalent Make | 51 | Nos
2 | Supply of recess mounted down light fitting with 15W LED lamps and suitable drivers.(Cat Ref. No. - CROMPTON LCDD-15-CDL/TL/WW) or Approved Equivalent Make | 223 | Nos
3 | Supply of Surface mounted inderect strip light fitting with 5W LED lamps and suitable drivers for cove lighting. | 20 | Nos
4 | Supply of Surface mounted down light fitting with 15 W or 12W LED lamps and sutable drivers.(Cat Ref. No. - CROMPTON LCDSPL-R-12-CDL) or Approved Equivalent Make | 6 | Nos
5 | Supply of Wall mounted down light fitting with 9W or 10W LED lamps and sutable drivers for Mirror light fitting. | 5 | Nos
6 | Supply of LED Batten with 20W Tube with system efficacy of 100Lm/W , delivering 1800Lumens. | 2 | Nos
Total value of Light Fixtures

## HVAC
SBI LIFE INSURANCE CO LTD
PROPOSED INTERIOR WORKS FOR SBI LIFE, REGIONAL OFFICE AT KODAMBAKKAM, CHENNAI
BILL OF QUANTITIES - HVAC WORKS
S. No. | Description | Qty | Unit | Rate | Amount
1 | Supply and laying of galvanized sheet steel ducting with class VIII quality of zinc coating, complete with anchor fasteners and MS supports, angle bracings as required, nut, bolt & gasket etc
| a. 24 G ducting: | 175 | sqM.
| b. 22 G ducting: | 340 | sqM.
| c. 20 G ducting: | 80 | sqM.
2 | Supply and laying of thermal insulation of ducting with 12 mm thick nitrile rubber, laminated with Aluminium foil | 90 | sqM.
3 | Supply and fixing of Aluminium powder coated supply air grills
and return air grills
| SAG with collar damper | 8 | sqm
| RAG without damper | 25 | sqm
4 | Acoustic insulation of duct with nitrile rubber | 125 | sqm
5 | Servicing and cleaning of the existing AC units | 4 | sets
6 | Providing bird screen at the opening of the outdoor
| units | 2 | sets
7 | Cassette Air-conditioners
Supply, Installation, Testing and Commissioning of Inverter Type, Full Copper, Refrigerant Cassette Air-conditioners of below mentioned tonnage capacity with On-Off Timer along with wireless remote controller. The rate shall include necessary refrigerant,including necessary refrigerant charge for the length between IDU to ODU.
i) IDU consisting of evaporator coil, BLDC Fan Motor, filters, insulated drain pan, drain pump, One motor per vane in Indoor unit to control each of the four vanes independently, etc
ii) ODU consisting of hermatically sealed Compressor to operate on 230 V, Single Phase, 50 Hz AC Supply, Anti Corrosive Coated Copper Condensor Coil with fan and motor, interconnecting refrigeration piping, starters/controls/cutouts/relays etc., mounted inside a powder coated sheet metal cabinet duly treated for corrosion protection. Acceptable makes: Toshiba, O-General, Misubishi, Daikin, Hitachi-
a | 3 TR For RD Room | 1 | set
b | 2 TR for Server room / UPS room | 4 | set
c | Outdoor unit brackets | 5 | sets
d | Refrigeration piping | 100 | M
e | Electrical wiring | 100 | M
f | Voltage stabiliser | 4 | sets
g | Remote controller | 5 | nos
h | Automatic timer for 24 hours operation | 2 | sets
GRAND TOTAL HVAC WORKS

## F
STATE BANK OF INDIA
PROPOSED INTERIOR WORKS FOR SBI LIFE, REGIONAL OFFICE AT KODAMBAKKAM, CHENNAI
BILL OF QUANTITIES - FIRE DETECTION AND FIRE ALARM SYSTEM
S. No. | Description | Qty | Unit | Rate | Amount
1 | Supply, Installation, Testing and Commissioning (SITC) of a Standalone micro processor based conventional type fire alarm panel, of 4 zones, with provision expandable up to 6 zones complete with battery back up for 8 hours of operation of the panel with 30% of the detectors in operation. | 1 | No
2 | SITC of Multicriteria smoke cum heat detectors below the false ceiling | 35 | Nos
3 | SITC of Multicriteria smoke cum heat detectors above the false ceiling | 32 | Nos
4 | SITC of manual call point near exits | 2 | Nos
5 | SITC of dual tone electronic hooter | 2 | Nos
6 | SITC of response indicators | 32 | Nos
7 | SITC of Heat Detector | 2 | Nos
8 | Supplying and laying of interconnecting copper cabling of 2 x 1.5 sqmm FRLS cable | 600 | Mtr
GRAND TOTAL FAS WORKS

## SS
STATE BANK OF INDIA
PROPOSED INTERIOR WORKS FOR SBI LIFE, REGIONAL OFFICE AT KODAMBAKKAM, CHENNAI
BILL OF QUANTITIES - SPRINKLER SYSTEM
S. No. | Description | Qty | Unit | Rate | Amount
1 | Providing and fixing of MS ‘C’ class heavy duty sprinkler piping with welded joints including all fittings, fixed on the ceiling with MS brackets at every 2500 mm. The entire piping system shall be pressure tested to a pressure of 15 Kg/ sq.cm and held for 4 hours. The pipe and supports, after pressure testing, are to be applied with one coat of zinc chromate primer paint and two coats of PO red synthetic enamel paint. The piping system shall be done as per the directions of engineer in charge.
| a) 80 mm dia: | 74 | M
| b) 65 mm dia: | 36 | M
| c) 50 mm dia: | 36 | M
| d) 40 mm dia: | 40 | M
| e) 32 mm dia: | 40 | M
| f) 25 mm dia: | 90 | M
Supply, erection and commissioning of SS sprinklers of 68 deg C fire rating, complete with fixing to the sprinkler pipe as under:
2 | a. Pendant type sprinkler | 98 | nos.
3 | Supply and laying of metallic flexible hose of suitable dia and about 900 mm long for fixing the sprinklers to the main pipe wherever false ceilings are provided. | 98 | nos.
4 | Water flow switch | 1 | nos.
GRAND TOTAL