## AE
BILL OF QUANTTITES FOR ELECTRICAL WORKS TO SBI LIFE, VIJAYAWADA.
S No. | Description | ROOM | SHED NO.1 | SHED NO.3 | SHED NO.4 | QTY | Unit | Rate | Amount
1 | a) Supply, installation, Testing and Commissioning of 3 phase and Neutral 415V 4 wire Free Standing Floor mounted MVpanel made out of 14 SWG MS sheet after seven tankprocess and painting with Epoxy powder coating. The panel shall consist of suitable rating TPN Aluminium busbar (at the rating of 0.8A/Sq.mm) supported with DMC/ SMC insulators and color coded with Heat shrinkable sleeves.TheMetering shall be provided as specified. The panel shall have Short circuit withstanding capacity of minimum 35KA and consist of the switchgear as mentioned below. The panel shall be got fabricated from manufacturers with CPRI Test certificate only. The PCC shall have atleast two spare cubicles of the maximum rating. The size of all PanelMounting Meters shall be 96X96mm. The Panels shall be mounted on U channels including supply and fixing of the same. |  |  |  |  | 1 | No
BUS BAR
TPN Alluminium busbar of 400A with 35KA fault level capacity, mounted on non-hygroscopic, glass fibre reinforced insulators-1Set
INCOMER
315A, 35KA FP MCCB (Thermal release) - 1no
2A, control fuse - 3 Nos.
RYB indicating lamps - 1 Set
315/5A, CL-1, 15VA CT's with tape wound - 3 nos.
KWH Meter
Surge Protection Device L&T make Type 1+2 Imax-50kA, 3P+N cat no.AUSP123PN50 -1No.
Neutral failure relay, L&T make- 1 No.
OUTGOINGS
63A, 10KA FP MCBs - 6nos ( PDBs - 4 Nos, Spare - 2 Nos)
40A, 10KA FP MCBs - 6nos ( LDBs- 4 Nos, Spare- 2 Nos)
32A, 10KA FP MCBs - 12nos ( Cassette AC units- 10 Nos, Spare- 2 Nos)
100A, 25KA FP MCCBs (Thermal release) - 2no ( UPS Input and APFC)
APFC
. BUS BAR TPN Aluminium busbar of 125A with 25 KA fault level capacity, mounted on non-hygroscopic, glass fibre reinforced insulators-1Set Automatic Power factor controller with 6channel for controlling the capacitor bank Outgoings- 4nos 10 KVAR MD type Capacitor bank -2nos 5 KVAR MD type Capacitor bank, 40A TP MCB 10kA - 4 Nos, 25A TP MCB, 10kA - 2Nos 40 A FP contactor - 04nos and 25A FP contactor - 2 Nos.
Two numbers of earthing terminals - one on each side of the panel with earth strip run inside the panel
2 | Supply and fixing of 315 A FP MCCB, 25KA in factory made sheet steel enclosure with all accessories etc., complete |  |  |  |  | 1 | No
3 | Supply, laying and commissioning of following size 1.1KVgrade XLPE insulated armoured aluminium conductor underground cable, in built up cable trench/ already laid RCChume pipe or on cable tray with all installation materials.When the cable is to be laid in ground, the same shall be laid at a depth of 750mm below ground level including excavation and refilling of earth after cables are laid,providing protection with sand and bricks at sides and top and cable route markers at 'every 15mtr. interval and also at the turnings. The cable shall conform to IS .
| a) 3.5C X 240 Sq.mm in Ground | 80 |  | 80 |  | 20 | Rmt
| b) 3.5C X 240 Sq.mm in existing tench / hume pipe/ on Surface | 20 |  | 20 |  | 80 | Rmt
c | Supply, laying and commissioning of following size 1.1KVgrade XLPE insulated armoured aluminium/ copper conductor underground cable, in built up cable trench/ already laid RCChume pipe or on cable tray or on surface with saddles, screws etc., with all installation materials ( for AC Outdoor Units )
| a)4C X 6Sq.mm Copper | 200 | 200 | 140 | 250 | 50 | Rmt
| b)4C X 10 Sq.mm Copper | 50 | 50 | 25 | 100 | 100 | Rmt
4 | Providing Indoor ordinary end terminations for the cable specified above with compression type steel gland,Bi-metallic lugs using crimping tool,Insulation tape,Identification tags etc., including end termination.
i | a) 3.5C X240 Sq.mm | 2 |  | 2 |  | 4 | No
ii | ii) Providing Indoor ordinary end terminations for the cable specified above with compression type steel gland,Bi-metallic lugs using crimping tool,Insulation tape,Identification tags etc., including end termination.
| a)4C X 6 Sq.mm Copper | 24 | 24 | 22 | 60 | 4 | No
| b)4C X 10 Sq.mm Copper | 2 | 2 | 2 | 2 | 6 | No
5 | a)Providing GI Earth station, with 40 mm Class B GI pipe at 2500mm depth including construction of brick pedestal, providing meshed funnel,CI cover and other civil Engineering works, spreading a homogenous mixture of salt,charcoal around the pipe etc,completely as per IS3043,1987 or latest revision. | 2 | 2 | 2 | 2 | 2 | Nos
6 | b) Supply and laying of following size strips including including all necessary inter connections with earth station and equipments.
| i) 25 mm X 5mm Hot dip GI strip | 20 | 20 | 20 | 20 | 40 | Meter
7 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete :
| 100 mm dia. R.C.C. pipe | 10 | 20 | 20 | 20 | 10 | Meter
8 | Supply, Installation, Testing & Commissioning ( S.I.T.C ) of all items described below should be Factory Manufactured & Tested & ISI marked. Proposed location & route should be as per the drawing. However, if any obstruction in encountered at site suitable modification may be made as per site condition. After completion of work the contractor must supply 3 copies of " As Built " drawing of actual route & location of items. All UPS & Raw Power points to be marked as U1,U2...& RP 1, RP2 etc., on each work station / Desk etc., Similarly load/ points connected on each MCB to be indicated with a chart pasted inside the cover of each distribution board. Insulation testing of wiring with megger & Testing of ELCB with Test lamp should be carried out before charging system & insulation test report as well as RCCB/RCBO test report to be submitted with the Bill. Load shall be equally Balanced on 3 phases. All DBs and UPS+Raw power points should have an earth wire connection in their socket earth terminal.
Distribution System
S.I.T.C of Factory Manufactured single / 3 phase & Neutral Double door distribution board made out of 16 SWG sheet steel enclosure with cutouts for operating MCB/ MCCB/RCCB etc knobs & consisting of Phase, Neutrl & Earth busbars with tapped holes, phase barriers & covers with removable plates on Top & Bottom for Incoming & Outgoing cables. DBs shall be flush mounting type for both single & three phase. All wires / cables should be terminated with Ring / PIN type copper lugs in each MCB in DB as well as in each of Neutral & earth link strips.
a) S.I.T.C of L.D.B
| S.I.T.C of Three Phase 4 way Double door Horizontal D.B. with Four pole 30Milliamp 32 Amp RCBO as incomer - 1No. 6Amp S.P. Amp M.C.B. - 12Nos with all wiring connections |  |  |  |  | 4 | No
b) S.I.T.C of RPDB
| S.I.T.C of Three Phase 12 way Double door Horizontal D.B. with Four pole 100 Milliamp 63 Amp RCBO as incomer - 36Nos. 6-25Amp S.P. Amp M.C.B. - 36Nos with all wiring connections |  |  |  |  | 4 | No
c) UPS DB ( Input )
| Supply and fixing of 80A FP MCB, 10KA in factory made sheet steel enclosure with all accessories etc., complete |  |  |  |  | 1 | No
d) UPS DB ( Output )
| S.I.T.C of Three Phase 4 way Double door Vertical type D.B. with Four pole 80Amp MCB,10KAas incomer - 1No. 40Amp S.P. Amp M.C.B. - 6Nos with all wiring connections |  |  |  |  | 1 | No
e) S.I.T.C of UPS SDB
| S.I.T.C of Single Phase 12 way Double door Horizontal D.B. with Double pole 40 Amp MCB, 10KA as incomer - 1No. 6-16Amp S.P. Amp M.C.B. - 12Nos with all wiring connections |  |  |  |  | 5 | No
| g)Supply, fixing testing and commissioning of factory made 16A Single phase socket with 16A SPMCB in MS box including all fixing accessories.( for 1.0Tr ACs ) |  |  |  |  | 9 | No
| g)Supply, fixing testing and commissioning of factory made 20A Single phase socket with 20A SPMCB in MS box including all fixing accessories.( for 1.5Tr ACs ) |  |  |  |  | 12 | No
| h)Supply, fixing testing and commissioning of factory made 25A Single phase socket with 25A DPMCB in MS box including all fixing accessories.( for 2Tr ACs ) |  |  |  |  | 7 | No
| i) Supply fixing, testing and commissioning of factory made 32 A 3p+N+e Metalclad socket with 32A 3P MCB in MS box including all fixing accessories. |  |  |  |  | 10 | No
9 | Sub - Mains Cabling & Wiring : For Lighting, Raw Power & U.P.S.DBs.
S. I. T.C of I.S.I marked 1.1KV grade multi-strand F.R.L.S Copper P.V.C wires in 19/25/32/40/50 mm Medium grade I.S.I marked PVC pipes to be laid in Underground trench / On wall / above false ceiling etc complete with all conduit accessories like bends, tees, junction boxes with necessary fixing hardware etc including re-surfacing of the floor/ wall etc. wherever necessary with Resufacing material.
| a) S.I.T.C of bunch of 4 X 16 Sqmm FRLS Copper wire with 2 X 10 sq mm FRLS Copper earth to be laid together in 50mm PVC conduit from UPS Input to UPS and UPS to UPS Output DB. And connection with check nuts etc., D.B. body to be earthed with double earth. End termination of above cable with suitable Copper lugs on both side of cable ( pin type ) |  |  |  |  | 20 | Meter
| b) S.I.T.C of bunch of 4 X 6 Sqmm FRLS Copper wire with 2 X 4 sq mm FRLS Copper earth to be laid together in 40mm PVC conduit from Main panel to PDBs and 32 A Socket. And connection with check nuts etc., D.B. body to be earthed with double earth. End termination of above cable with suitable Copper lugs on both side of cable ( pin type ) |  |  |  |  | 520 | Meter
| c)S.I.T.C of bunch of 4 X 4Sqmm. F.R.L.S Copper flexible wires with 2 X 2.5sq mm FRLS Copper earth to be laid together in 32mm PVC conduit from Main Panel to LDBs. ( body to be earthed ) End termination of above wires at both ends in DBs with pin type copper lugs. |  |  |  |  | 120 | Meter
| d)S.I.T.C of bunch of 2 X 6 Sqmm. F.R.L.S Copper flexible wires with 1 X 4sq mm FRLS Copper earth to be laid together in 25mm PVC conduit from UPS Output DB to UPS SDB. ( body to be earthed ) End termination of above wires at both ends in DBs with pin type copper lugs. |  |  |  |  | 150 | Meter
| e)S.I.T.C of bunch of 2 X 4 Sqmm. F.R.L.S Copper flexible wires with 1 X 2.5 sq mm FRLS Copper earth to be laid together in 25mm PVC conduit from RPDB to 16A socket/ 25A socket. ( body to be earthed ) End termination of above wires at both ends in DBs with pin type copper lugs. |  |  |  |  | 1140 | Meter
| f)S.I.T.C of bunch of 2 X 2.5 Sqmm. F.R.L.S Copper flexible wires with 1 X 1.5 sq mm FRLS Copper earth to be laid together in 25mm PVC conduit from RPDB to 6A DP MCB/ 6A socket. ( body to be earthed ) End termination of above wires at both ends in DBs with pin type copper lugs. |  |  |  |  | 475 | Meter
10 | S.I.T.C of I.S.I marked 1.1KV grade multi- strand F.R.L.S Copper P.V.C wires in 19/25mm Medium grade I.S.I marked PVC pipes to be laid in Underground trench/ On wall / above false ceiling / Through Modular Furniture slots etc complete with all conduit accessories like bends, tees, Junction boxes with necessary fixing hardware etc., including resurfacing of the floor/ wall etc., wherever necessary with Resurfacing material. Point wiring for Lights fans, exhaust fans 6 Amps depedent socket outlets etc., using S & I of 3 X 1.5 Sq.mm, Flexible copper FRLS multi- strand PVC copper wires in PVC conduits as described above for all the following points. Point wiring to include cost of wiring in PVC conduits & switch, sockets, boxes, plates & fixing accessories.
| a) Single light points/ Exhaust Fan controlled by 6 Amp switch |  |  |  |  | 19 | No
| b) Two light points controlled by one 6 Amp switch |  |  |  |  | 30 | No
| c) Three Light points controlled by one 6 Amp Switch |  |  |  |  | 60 | No
| d) Dependant 6 Amp 3/5 Pin combination type Universal socket with indicator mounted on switch-box ( except toilets & passages ) |  |  |  |  | 50 | No
| e) Fan Points |  |  |  |  | 14 | No
| f) S.I.T.C of Light point with Timer for Sign board |  |  |  |  | 1 | No
11 | Raw & UPS points
| a) S.I.T.C of Recessed 6 Amp 5 Pin Universal Sockets controlled by one 6 Amp Indicator switch complete with Flush surface plate for Raw Power on Work stations. ( Above work table area ) etc, Wires to be drawn from Wire / Cable manager/ Channel inside the work station from underground metal box containing the conduits located below the work-station. No surface conduit to be seen below work station. |  |  |  |  | 106 | No
| b) S.I.T.C of 3 Nos of 6 Amp Universal Sockets controlled by one 16Amp Indicator switch housed in a Modular PVC switch box with recessed surface plate for UPS Switch pts on Work stations. ( 3 Nos sockets in box with surface plate will be below table. Only 16Amp Control switch for these points with Recessed Surface Plate will be above table. All wires to be drawn through cable/ wire channel inside work station. No surface conduit/ casing to be seen below work station. Conduit junction boxess should below work station table & not below chair. |  |  |  |  | 106 | No
| c) S.I.T.C of Raw power point with modular 16Amp Switch and socket on modular front plate on GI box |  |  |  |  | 29 | No
| d) S.I.T.C of UPS point with 2Nos modular 16Amp Switch and socket on modular front plate on GI box in server room |  |  |  |  | 3 | No
CIRCUIT WIRING ( Lighting Switch Boards ) + UPS Pt. + R.P. Points.
12 | S.I.T.C of 3 X 2.5 Sq mm F.R.L.S copper flexible PVC wires lain in 19/20mm Middle gauge PVC conduits laid on wall / above false ceiling / Concealed as per requirement with all accessories etc., LDB to switch boards & From UPS OPDB to work station + From R.P.D.B to R.P. Pts on work station ( Maximum 2 Nos of UPS & Raw power points to be connected on one circuit.) |  |  |  |  | 2000 | Meter
13 | LIGHTING FIXTURES
| a) S.I.T.C of 6.7 W LED luminaire similar to CAT NO.DN191B LED6S-6500 PSU WH S1 PHILIPS Make |  |  |  |  | 30 | No
| b) S.I.T.C of 12.3W LED Luminaire similar to CAT NO.DN193B LED12S-6500 PSU WH S1 PHILIPS Make |  |  |  |  | 163 | No
| c) S.I.T.C of 30 W LED Luminaire similar to CAT NO RC380B LED30S-6500 L60W60 PSU PHILIPS Make |  |  |  |  | 66 | No
14 | Security System:
| a) S & I of 4" X 4" Red Danger Mark Stickers 230Volt / 440 Volt etc to be fixed on all the DBs. S&I of |  |  |  |  | 15 | No
| b) S & I of 4.5K.G. CO2 Fire Extinguisher |  |  |  |  | 10 | No
| c) 4.5 KG ABC Fire Extinguisher |  |  |  |  | 10 | No
Earthing System
15 | a)Providing Copper Earth station, with 600X600X3mm Copper plate at 2700mm depth including construction ofbrick pedestal, providing meshed funnel,CI cover and other civil Engineering works, spreading a homogenous mixture ofsalt,charcoal around the pipe etc,completely as per IS3043,1987 or latest revision. |  |  |  |  | 2 | No
16 | b) Supply and laying of following size strips including including all necessary inter connections with earth station and equipments including excavation and back filling etc complete.
| i) 25mm x 5mm Copper strip |  |  |  |  | 40 | Meter
DG Set Accessories
17 | 4 pole 315 Amp Manual on load Changeover Switch in sheet steel enclosure mounted on suitable angle iron frame for Mains to D.G. supply switching ( if D.G. Back up is provided ) depending upon load. |  |  |  |  | 1 | No
18 | LAN & Telephone Accessories
| a) 25mm PVC conduit pipe for laying Telephone Line from Tel. Tag block to each work station. |  |  |  |  | 450 | Meter
19 | Supply, fixing, testing and commissioning of Telephone outlet (RJ11) with anodised GI box with front plate and plug in type telephone socket . |  |  |  |  | 69 | Nos
20 | Supply, layingj, testing and commissioning of 2pair 0.5mm dia PVC insulated Copper conductor Telephone wire conforming to DOT Specification | 400 | RMT | 0 | 0 | 2800 | Meter
21 | Supply, installation, testing and commissioning of 10 pair Krone connectors in junction box complete as required.
| a)100 pair | 5 | NOS | 0 | 0 | 1 | Nos
22 | Supply, laying, testing and commissioning of 50pair 0.5mm dia jelly filled copper conductor armoured cables. | 100 | RMT | 3547.139 | 354713.904 | 100 | Meter
23 | Supply and Laying of 4Pair, UTP CAT 6 Lan Cable with all connections etc All Cable Numbers to be Provided at both ends. Both ends shall be with crimping | 109 | Pts | 1365 | 148785 | 109 | Pts
24 | Supply and fixing of RJ 45 , CAT 6 Information outlets | 109 | Nos | 455 | 49595 | 109 | Nos
25 | Supply of 7 feet Patch Cords Factory Crimping CAT 6 | 95 | Nos | 273 | 25935 | 95 | Nos
26 | Supply of 3 feet Patch Cords Factory Crimping CAT 6 | 108 | Nos | 247 | 26676 | 108 | Nos
27 | Supply and Fixing of 24 Port CAT 6 Jack Panel, | 4 | Nos | 7800 | 31200 | 4 | Nos
28 | Supply and fixing of 24 Port 10/100mbps D Link Switch | 4 | Nos | 5460 | 21840 | 4 | Nos
29 | Supply and fixing of 9U Rack with Acceries(Self, Power Manager, Cable Manager, Fan etc) | 3 | Nos | 7800 | 23400 | 3 | Nos
30 | Cutting/ Chasing of Floor of following sizes of laying of Conduits as per site conditions.
| 1. 12" X 12" Size |  |  |  |  | 80 | No
| 2. 8" X 8" Size |  |  |  |  | 80 | No
| 3. 6" X 6" Size |  |  |  |  | 80 | No
| 4. 4" X 4" Size |  |  |  |  | 80 | No
31 | S & I of Metallic Boxes with Steel Surface Plates fixed with Steel screws.
| 1. 12" X 12" |  |  |  |  | 10 | No
| 2. 8" X 8" |  |  |  |  | 10 | No
| 3. 6" X 6" |  |  |  |  | 10 | No
| 4. 4" X 4" |  |  |  |  | 10 | No
32 | i) S.I.T.C of U-PVC Trunking with cover plate & other accessories Legrad / Precision make
| a) S.I.T.C. of 80X 50mm DLP U-PVC trunking system with all accessories. |  |  |  |  | 80 | Meter
| b) S.I.T.C. of 32X 20mm DLP U-PVC trunking system with all accessories. |  |  |  |  | 80 | Meter
| c) S.I.T.C. of 32X 12.5mm DLP U-PVC trunking system with all accessories. |  |  |  |  | 80 | Meter
ii) S.I.T.C of GI Raceways with fixing brackets and all necessary accessories etc., complete. Legrand
| a) 150mm x 38mm 1 compartment |  |  |  |  | 120 | Meter
| b) 225mm X 38mm 3 Compartment |  |  |  |  | 120 | Meter
| c) 300mm X 38mm 3 Compartment |  |  |  |  | 120 | Meter
iii) S.IT.C. of Height adjustable raceway junction box with flyover for direct access to cables at intersection while maintaining perfect separation and 90 deg cross over between data and power cables with all fixing accessories etc., complete. Legrand
| a) 225mm X 225mm X 65-90mm with flyover |  |  |  |  | 10 | No
| b) 300mm X 300mm X 65-90mm with flyover |  |  |  |  | 10 | No
| c) 400mm X 400mm X 65-90mm with flyover |  |  |  |  | 10 | No
33 | Ceiling / Exhaust Fan:
| a) S.I.T.C of 6" Exhaust Fan as per size of Toilet/ UPS/ Server Room Windows. |  |  |  |  | 8 | No
| b) S.I.T.C of High Breeze 48" Ceiling fans with 100W Electronic regulator. |  |  |  |  | 1 | No
| c) S.I.T.C of High Breeze 36" Ceiling fans with 100W Electronic regulator. |  |  |  |  | 1 | No
| d) S.I.T.C of High Breeze 24" Ceiling fans( UPS room) with 100W Electronic regulator. |  |  |  |  | 1 | No
| e) S.I.T.C of 16" Wall mounted Fans - 2 Nos for Server+ UPS rooms. Only Fan Points to be provided at other locations as stated in item no.3e ( Branch will provide the fans as per their need at later date ) |  |  |  |  | 3 | No
34 | Miscellenous Items
| a) S.I.T.C of Bell with Bell Point for BSM/ Area Manager |  |  |  |  | 5 | No
| b) S.I.T.C of Timer with MCB control for Sign Board of Branch. |  |  |  |  | 1 | No
IMPORTANT Note : Successful / L1 contractor has to strictly use only Approved Make of materials. Final as built CAD drawings ( 3 sets ) with Measurement Sheets ( D.B. to Each Switch board + DB to each AC + DB to each UPS & Raw Points etc., and clearly showing conduit routes for Lighting, UPS & Raw + LAN cabling and indicating the points looped on one circuit + Marking of UPS and RAW Pts on each work station and Pasting of Chart in each D.B. Indicating the circuit have to be enclosed with Final bill. All above requirements are mandatory without which final bill will not be processed. Payment Will be made as per Actual Measurements for which Measurement sheet is essential. No Extra items to be executed without prior intimation / approval.
Electrical works Total
35 | IP Phones:
a | Supply, installation, testing and commissioning of HTEK UC902 UC902 which delivers superior HD audio quality, rich and leading edge telephony features etc. with the following features |  |  |  |  | 70 | Nos
Phone Features ● 2 SIP accounts ● Call hold, mute, DND ● One-touch speed dial, hotline ● Call forward, call waiting, call transfer ● Redial, call return, auto answer, direct IP call ● 5-way conferencing ● Group listening, SMS, emergency call ● Ring tone selection/provisioning ● Set date time automatically or manually ● Dial plan per account ● RTCP-XR (RFC3611), VQ-RTCPXR (RFC6035) ● Action URL/URI
Voice Codecs Features ● HD voice: HD handset, HD speaker ● Codecs: iLBC, G.722, G.711(A/μ), ● GSM_FR, G.723, G.729AB, G.726-32 ● DTMF: In-band, RFC 2833, SIP INFO ● Full-duplex hands-free speakerphone with AEC ● VAD, AGC, CNG, AEC, PLC, AJB Directory ● Local phonebook up to 1000 entries ● XML/LDAP remote phonebook ● Intelligent search method ● Phonebook search/import/export ● Call history: dialed/received/missed/forwarded ● Black list
Feature keys ● 2 line keys with LED ● 6 features keys: mute, headset, message, ● 4 context-sensitive “soft” keys ● transfer, redial, speaker ● 6 navigation keys ● Volume control keys Interface ● Dual-port 10/100M Ethernet ● Power over Ethernet (IEEE 802.3af), class 2 ● 1xRJ9 (4P4C) handset port ● 1xRJ9 (4P4C) headset port Physical Features ● Stand with 2 adjustable angles ● Wall mountable ● AC adapter : 100~240V input and DC 5V/1.2A output ● Power consumption (PSU): 1.6~2.6W ● Power consumption (PoE): 2.0~3.2W ● Operating humidity: 10~95% ● Operating temperature: -10~50°C
Management ● Configuration: browser/LCD-Menu/auto-provision ● Auto provision via HTTP/HTTPS FTP/TFTP ● Auto-provision with PnP ● Reset to factory, restart, reboot ● Local tracing log export, system log ● Phone lock for personal privacy protection Network and Security ● SIP v1 (RFC2543), v2 (RFC3261) ● SIP server/proxy redundancy ● NAT Traversal: STUN mode ● DHCP/static/PPPoE/IEEE802.1X/open VPN ● HTTP/HTTPS web server ● Time and date synchronization by SNTP ● DNS-NAPTR/DNS-SRV(RFC 3263) ● QoS: 802.1p/Q tagging (VLAN), Layer 3 ToS DSCP ● TLS(Transport Layer Security), SRTP ● HTTPS certificate manager ● AES encryption for configuration file ● Digest authentication using MD5/MD5-sess
b | Supply, installation, testing and commissioning of HTEK UC903 UC903 with superior HD audio quality, rich and leading edge telephony features, all the functions of software with the following features |  |  |  |  | 12 | Nos
Phone Features ● 3 SIP accounts ● Call hold, mute, DND ● One-touch speed dial, hotline ● Call forward, call waiting, call transfer ● Redial, call return, auto answer, direct IP call ● 5-way conferencing ● Group listening, SMS, emergency call ● Ring tone selection/provisioning ● Set date time automatically or manually ● Dial plan per account ● RTCP-XR (RFC3611), VQ-RTCPXR (RFC6035) ● Action URL/URI Voice Codecs Features ● HD voice: HD handset, HD speaker ● Codecs: iLBC, G.722, G.711(A/μ), ● GSM_FR, G.723, G.729AB, G.726-32 ● DTMF: In-band, RFC 2833, SIP INFO ● Full-duplex hands-free speakerphone with AEC ● VAD, AGC, CNG, AEC, PLC, AJB
Directory ● Local phonebook up to 1000 entries ● XML/LDAP remote phonebook ● Intelligent search method ● Phonebook search/import/export ● Call history: dialed/received/missed/forwarded ● Black list IP-PBX Features ● Busy Lamp Field (BLF), bridged Line Appearance(BLA) ● Anonymous call, anonymous call rejection ● Message Waiting Indicator (MWI) , voice mail ● Intercom, paging ● Call park, call pickup ● Music on hold ● Hot-desking Display and Indicator ● 192x64 pixel graphical LCD with backlight ● LED for call and message waiting indication ● Illuminated LEDs for line status information ● Intuitive user interface with icons and soft keys ● National language selection ● Caller ID with name, number
Feature keys ● 6 line keys with LED ● Paperless DSS keys up to 20 various features ● 8 features keys: voice mail, headset, mute, ● 4 context-sensitive “soft” keys ●speaker, conference, hold, transfer,redial, ● 6 navigation keys ● Volume control keys Interface ● Dual-port 10/100M Ethernet ● Power over Ethernet (IEEE 802.3af), class 2 ● 1xRJ9 (4P4C) handset port ● 1xRJ9 (4P4C) headset port Physical Features ● Stand with 2 adjustable angles ● Wall mountable ● AC adapter : 100~240V input and DC 5V/1.2A output ● Power consumption (PSU): 1.6~2.6W ● Power consumption (PoE): 2.0~3.2W ● Operating humidity: 10~95% ● Operating temperature: -10~50°C
Management ● Configuration: browser/LCD-Menu/auto-provision ● Auto provision via HTTP/HTTPS FTP/TFTP ● Auto-provision with PnP ● Reset to factory, restart, reboot ● Local tracing log export, system log ● Phone lock for personal privacy protection Network and Security ● SIP v1 (RFC2543), v2 (RFC3261) ● SIP server/proxy redundancy ● NAT Traversal: STUN mode ● DHCP/static/PPPoE/IEEE802.1X/open VPN ● HTTP/HTTPS web server ● Time and date synchronization by SNTP ● DNS-NAPTR/DNS-SRV(RFC 3263) ● QoS: 802.1p/Q tagging (VLAN), Layer 3 ToS DSCP ● TLS(Transport Layer Security), SRTP ● HTTPS certificate manager ● AES encryption for configuration file ● Digest authentication using MD5/MD5-sess
c | Supply of IP PBX for Up to 200 Extensions Up to 60 Simultaneous Calls Up to 40 Simultaneous Conference Attendees Up to 36 Call Queues Up to 36 Conference Rooms Recording up to 150 hrs (WAV) Recording up to 1500 hrs (GSM) Automatic Recording/One Touch Recording CDR (Call Detailed Recording) Multi-layer IVR (Interactive Voice Response) TDM/SIP/IAX Extensions/trunks Flexible Inbound/Outbound Routing Time-based Routing Remote Extensions & Remote Offices Paging & Intercom Video Call Call Forward/Transfer Web Extension (WebRTC) Follow Me DND (Do Not Disturb) Ring Groups Pick-up Groups DISA (Direct Inward System Access) Virtual Fax Voicemail to Email/Fax to Email One Number Stations Smart DID Media |  |  |  |  | 1 | Nos
Audio Codecs: G.722/G.711-Ulaw/G.711-Alaw/G.726/G.729/GSM/SPEEX Video Codecs: H.261/H.263/H.263+/H.264 Fax: T.38 (pass through)
Network & Protocols IPv4, IPv6, VLAN, DHCP, PPPoE, DDNS, SNMPv2, NTP, SNTP, TFTP, SSH, HTTPS, SRTP, TLS, LDAP, TR069
Security HTTPS, Fail2Ban, Permit IP, Whitelist, Blacklist VPN Server (PPTP, L2TP, OpenVPN, IPSec) VPN Client (N2N, PPTP, L2TP, OpenVPN, IPSec)
36 | IP Cameras:
a | Supply of IP Camera with 5MP with 30mtrs distance IP 360 rated water proof with reset button including cost and installation of all materials |  |  |  |  | 5 | Nos
b | Supply of NVR 8-ch nvr 8 channel net video recorder |  |  |  |  | 1 | Nos
c | Seagate Hard disk with all connectors |  |  |  |  | 1 | Nos
37 | Motion Sensor:
a | Supply of Motion detecting pir sensor |  |  |  |  | 13 | Nos
| Installation charges including all labour, accessories and materials complete including testing and commissioning | [5 empty] | LS
For IP phones & cameras
38 | Sound system with Mics
a | Supply, fixing, tyesting & commissioning of Sound system with for Conference room and Training hall including cost of labour and installation of all materials etc., for complete work.
| Sony VPL- CH 370 3 LCD projector (5000 ANSI LUMENS OF WUXGA, HD) |  |  |  |  | 1 | Nos
| 8'X5'6" Reverb Motorized screen 16:10 |  |  |  |  | 1 | Nos
| Beyer dynamic classis GM 305 Gooseneck micro phones |  |  |  |  | 11 | Nos
| BEYER dynamic GM 33S BASE UNIT FOR GOOSE NECK MICS WITH ON/OFF |  |  |  |  | 11 | Nos
| Biamp tesira forte AVB CI external codec conferencing |  |  |  |  | 1 | Nos
| Biamp AMP -A 460H Amplier |  |  |  |  | 1 | Nos
| QSC AC-C6T in-ceiling speakers: System Details AC-C6T Effective frequency range1 65 Hz – 20 kHz Rated noise power / voltage2 30 watts / 15.5 volts (RMS) Broad-band sensitivity3 89 dB SPL Coverage angle (-6 dB) 110° (500 Hz - 5 kHz) Maximum continuous SPL4 104 dB Maximum peak SPL4 110 dB, Rated bypass impedance 8 ohms, Transformer taps 70 V: 30, 15, 7.5, 3.7, 1.9 watts 100 V: 30, 15, 7.5, 3.8 watts, 8 ohm bypass HF transducer 22 mm [.86 in] silk dome tweeter, coaxially mounted, LF transducer 152 mm [6 in] Polypropylene cone with butyl rubber surround, Input connector type Euro block connector with parallel output terminals, Baffle material Painted ABS polymer, Grille material Painted steel, Back can material Galvanized steel, Testing Listed UL1480, UL2043 safe for use in air handling space, Net weight 3.5 kg [7.6 lb], Product dimensions Ø260 x 213 mm [Ø10.24 x 8.4 in], Cut-out Dimensions Ø229 mm [Ø9 in], Ceiling Capture Thickness 6.35 - 38.1 mm [0.25 - 1.5 in], Included accessories Rails & C-ring for ceiling tile installation, 1 Half-space, -10 dB from on-axis sensitivity 2 IEC60268-1 noise signal for 2 Hrs, 3 On-Axis, half-space sensitivity, 2.83V, 1 m 4 Calculated from rated noise voltage and sensitivity |  |  |  |  | 13 | Nos
| ATEN 4x2 HDMI SWITCHER VS482 |  |  |  |  | 1 | Nos
| ATEN 4x4 VGA/AUDIO SWITCHER VM0404 |  |  |  |  | 1 | Nos
| KRAMER PRESENTATION SCALER VP461 |  |  |  |  | 1 | Nos
| LOGIC CABLE CUBBIES |  |  |  |  | 3 | Nos
| DAC SPEAKER CABLE SPK 16 |  |  |  |  | 50 | MTRS
| DAC HDMI CABLE 15MTRS |  |  |  |  | 1 | Nos
| DAC HDMI CABLE 10MTRS |  |  |  |  | 2 | Nos
| VGA CABLE 10MTRS |  |  |  |  | 2 | Nos
| DAC HDMI CABLE 5MTRS |  |  |  |  | 2 | Nos
| VGA CABLE 5MTRS |  |  |  |  | 2 | Nos
| DAC HDMI CABLE 3MTRS |  |  |  |  | 1 | Nos
| VGA CABLE 3MTRS |  |  |  |  | 1 | Nos
| NT AUDIO CABLE |  |  |  |  | 110 | MTRS
| UNIVERSAL CEILING MOUNT KIT |  |  |  |  | 1 | Nos
| INTERCONNECT CABLES AND CONNECTORS |  |  |  |  | 1 | SET
SUBTOTAL
b | SECOND FLOOR TRAINING ROOM
| SONY VPL- EW 578 3 LCD projector (4200 ANSI LUMENS OF WUXGA, HD) |  |  |  |  | 1
| 10'X6'3" REVERB MOTORIZED SCREEN 16:10 |  |  |  |  | 1 | NOS
| SHURE PODIUM MIC |  |  |  |  | 1 | NOS
| SHURE CORDLESS HAND MIC |  |  |  |  | 2 | NOS
| SHURE CORDLESS COLLAR MIC |  |  |  |  | 1 | NOS
| APART AUDIO MASK6T WALL MOUNTED SPEAKERS |  |  |  |  | 8 | NOS
| APART AUDIO PA2240BPDUAL CHANNEL POWER AMPLIFIER |  |  |  |  | 1 | NOS
| YAMAHA MG 16XU MIXER |  |  |  |  | 1 | NOS
| DAC SPEAKER CABLE SPK 16 |  |  |  |  | 200 | MTRS
| DAC HDMI CABLE 20 MTRS |  |  |  |  | 2 | NOS
| VGA CABLE 20 MTRS |  |  |  |  | 2 | NOS
| NT AUDIO CABLE |  |  |  |  | 110 | MTRS
| UNIVERSAL CEILING MOUNT KIT |  |  |  |  | 1 | NOS
| INTERCONNECT CABLES AND CONNECTORS |  |  |  |  | 1 | SET
SUBTOTAL
39 | Supply, fixing, testing & commissioning of Security Access Control System including labour and installation of all materials etc., for complete work.
| Finger print and EM Prox card based door controller with battery backup and charger (Entry door controller) optical finger print and EM proximity card based reader, Supports access control and time - attendance, IP 65 Rating ( Water proof), 50,000 events and 9600 finger print template storage, Built in power over ethernet (POE), Built in door lock port, Door sense port, Exit reader, Exit switch port, RS-485 and Ethernet interfaces, Tri color LED and Buzzer, 12VDC Power supply through adapter or Battery backup. |  |  |  |  | 3 | Nos
| Finger print and EM Prox card based door reader (Exit Reader) optical finger print and EM Proximity card based reader, Wiegand / Rs-232 Interface IP 65rating (Waterpoof) Tamper detection, Tricolor LED Buzzer, 12VDC Power supply through adapter or Battery backup. Compatible with any COSEC Door controllers ( Except COSEC DOOR FOT) |  |  |  |  | 3 | Nos
| Matrix USB Dongle |  |  |  |  | 1 | Nos
| Matrix cosec GE Platform with 100 Users and expandable upto 500 users |  |  |  |  | 1 | Nos
| Matrix Cosec user 100 |  |  |  |  | 1 | Nos
| Matrix Cosec GE ATM - Time attandance management application |  |  |  |  | 1 | Nos
| Matrix Cosec GE ACM - Acess Control Management application |  |  |  |  | 1 | Nos
| Single wood door EM Lock |  |  |  |  | 1 | Nos
Total
GRAND TOTAL
s
40 | FIRE ALARM SYSTEM
1 | Supply,Testing and commissioning of the following number of Loops Microprocessor based addressable type (EN / UL approved) Fire alarm control panel with Zonal Indications, supervised inputs, supervised and non-supervised outputs,Zener barriers, two way media converter / Signal booster for in / out network connectivity with OF cableand with battery Power pack as per specifications.
| a) 2 - Loop | 1 | Nos | 219603 | 219603 | 1 | Nos
MULTI SENSOR DETECTORS
2 | Supply installation, testing and commissioning of analog addressable type multi sensor (smoke / heat) photo electric detectors with LED indication lamp. | 140 | Nos | 3779 | 529060 | 144 | Nos
ELECTRONIC HOOTERS:
3 | Supply, Installation, Testing and commissioning of analog addressable sounders with all fixing accessories. | 6 | Nos | 2824 | 16944 | 6 | Nos
MANUAL CALL POINTS:
4 | Supply and Installation of analogue addressable type Pull type Manual call Stations with monitor module | 4 | Nos | 3634 | 14536 | 4 | Nos
FAULT ISOLATION MODULE:
5 | Supply and installation fault isolator modules along with all fixing accessories. | 4 | Each | 3634 | 14536 | 4 | Each
CABLE:
6 | Supplying, testing and commissioning of 1100V grade FIRE RESITANCE LOW SMOKE PVC copper conductor twisted pair cables.
| a ) 25mm dia Heavy gauge FRLS PVC conduit | 500 | Rmt | 134 | 67000 | 500 | Rmt
| b ) Supply,laying,testing and commissioning of 2C x 1.5 sq.mm cable of 1.1 KV Grade XLPE , insulated, sheathed steel armoured with Copper Conductor Power Cables ( YWY ) should conform to IS 1554 ( Part I ). The rates quoted for laying shall include laying of cables on surface with saddles,screws etc. including material and labour charges etc complete as per site requirement. | 500 | Rmt | 171 | 85500 | 500 | Rmt
7 | Supply and fixing of Escape signage boards in Rigid Photo luminecent based glow in Dark rigid sheet with high intensity luminous properties with specificaiton. | 10 | Nos | 10676 | 106760 | 10 | Nos
8 | Supply and installation testing & commissioning of Input module.The rates quoted for laying shall include laying of cables on surface with saddles,screws including material and labour charges etc complete as per site requirement. | 3 | Nos | 3553 | 10659 | 3 | Nos
9 | Supply and installation of addressable Monitor module along with all fixing accessories. | 11 | Nos | 3452 | 37972 | 11 | Nos
10 | Supply, installation, testing and commissioning of Response indicators with all required accessories etc., complete. |  |  |  |  | 72 | Nos
| FIRE ALARM SYSTEM SUB TOTAL |  |  |  | 1102570
41 | FIRE FIGHTING
SPRINKLER SYSTEM
1 | FLEXIBLE DROP CONNECTION
| Supplying, installing, testing and commissioning flexible drop connections with 1.0 Mtr length to connect the pendent type Sprinkler | Nos. | 220 | 4500 | 990000 | 220 | nos
| FIRE FIGHTING SUB TOTAL |  |  |  | 1072750

## RATE ANALYSIS (hidden)
Rate Analysis for Item no.
SUB HEAD - 1 : INTERNAL ELECTRIFICATION
IE-1 | Point Wiring for Light/ Fan/ exhaust fan with 2runs of 1.1 kV grade FRLS PVC 1.5 Sq.mm & 1 run of 1.5 Sq.mm multi strand Copper wires , run in and including 25 mm dia Heavy duty PVC conduits concealed in wall / ceiling/above false ceiling conforming to IS including all accessories such as junction boxes, conduit bends elbows and ceiling rose, anodised GI Switch box with modular switch and the box covered with front plate.
POINT WIRING
Group C
COST FOR 1 POINT
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 1.5sq.mm Copper wire (2runs) LP 1330/ 90MTS | mtr | 13.15 | 14.7778 | 30% | 10.3444 |  |  |  | 0 | 10.3444 | 136.0294
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%)
= 13.15m
2 | Heavy Guage 25mm dia PVC Conduit | mtr | 4.73 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 109.6156
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
3 | 25mm dia PVC Bends | each | 1 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 6.5048
4 | 25mm PVC couplers | each | 2 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 0.441
5 | 25 mm iron staples/ saddles/ screws | each | 9 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 13.23
6 | 25mm dia PVC Junction boxes | each | 1 | 26.47 | 30% | 18.529 |  |  | 5% | 0.92645 | 19.4554 | 19.4554
7 | Metal box (2module) | each | 0.5 | 90 | 30% | 63 |  |  |  |  | 63 | 31.5
8 | switch plate (2module) | each | 0.5 | 150 | 30% | 105 |  |  |  |  | 105 | 52.5
9 | 6A switch (Legrand make 01 module) | each | 1 | 140 | 30% | 98 |  |  |  |  | 98 | 98
10 | PVC fastener 40mm long | each | 1 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 0.7
11 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 471.1263
12 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 9.4225
480.5488
13 | Installation,Testing and commissioning charges |  | 1 |  |  | 440.8 |  | 440.8 |  | 0 | 440.8 | 440.8
| WIREMAN G-1 | day | 0.3 | 579 |  | 173.7
| MASON G-2 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.4 | 523 |  | 209.2
440.8
921.3488
14 | Add 1% for Electricity Charges |  | S | [5 empty] | 1% |  |  | 9.2135
930.5623
15 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 139.5843
1070.1466
16 | Add 1% for WCT | [7 empty] | 1% |  |  | 10.7015
1080.8481
17 | Service Tax 6% | [7 empty] | 6% |  |  | 64.8509
1145.699
Rate per each
1146
| Say | [10 empty] | 1146
Rate Analysis for Item no.
COST FOR 1 POINT
b) Two Lights point controlled by one 6A switch.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 1.5sq.mm Copper wire (2runs) LP 1330/ 90MTS | mtr | 26.3 | 14.7778 | 30% | 10.3444 |  |  |  | 0 | 10.3444 | 272.0589
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%)
= 13.15m X 2
2 | Heavy Guage 25mm dia PVC Conduit | mtr | 9.46 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 219.2312
= 4.5 + 0.23 (wastage @ 5%) = 4.73m X 2
3 | 25mm dia PVC Bends | each | 2 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 13.0095
4 | 25mm PVC couplers | each | 4 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 0.882
5 | 25 mm iron staples/ saddles/ screws | each | 18 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 26.46
6 | 25mm dia PVC Junction boxes | each | 2 | 26.47 | 30% | 18.529 |  |  | 5% | 0.92645 | 19.4554 | 38.9109
7 | Metal box (2module) | each | 1 | 90 | 30% | 63 |  |  |  |  | 63 | 63
8 | switch plate (2module) | each | 1 | 150 | 30% | 105 |  |  |  |  | 105 | 105
9 | 6A switch (Legrand make 01 module) | each | 1 | 140 | 30% | 98 |  |  |  |  | 98 | 98
10 | PVC fastener 40mm long | each | 2 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 1.4
11 | Cement, paint, sand etc. | each | 2 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 6.3
| Total | [10 empty] | 844.2525
12 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 16.8851
861.1376
13 | Installation,Testing and commissioning charges |  | 1 |  |  | 661.2 |  | 661.2 |  | 0 | 661.2 | 661.2
| WIREMAN G-1 | day | 0.45 | 579 |  | 260.55
| MASON G-2 | day | 0.15 | 579 |  | 86.85
| KHALLASI | day | 0.6 | 523 |  | 313.8
661.2
1522.3376
14 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 15.2234
1537.561
15 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 230.6341
1768.1951
16 | Add 1% for WCT | [7 empty] | 1% |  |  | 17.682
1785.8771
17 | Service Tax 6% | [7 empty] | 6% |  |  | 107.1526
1893.0297
Rate per each
1893
| Say | [10 empty] | 1893
Rate Analysis for Item no.
COST FOR 1 POINT
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 1.5sq.mm Copper wire (2runs) LP 1330/ 90MTS | mtr | 39.45 | 14.7778 | 30% | 10.3444 |  |  |  | 0 | 10.3444 | 408.0883
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%)
= 13.15m X 3
2 | Heavy Guage 25mm dia PVC Conduit | mtr | 14.19 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 328.8469
= 4.5 + 0.23 (wastage @ 5%) = 4.73m X 3
3 | 25mm dia PVC Bends | each | 3 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 19.5143
4 | 25mm PVC couplers | each | 6 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 1.323
5 | 25 mm iron staples/ saddles/ screws | each | 27 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 39.69
6 | 25mm dia PVC Junction boxes | each | 3 | 26.47 | 30% | 18.529 |  |  | 5% | 0.92645 | 19.4554 | 58.3663
7 | Metal box (2module) | each | 1.5 | 90 | 30% | 63 |  |  |  |  | 63 | 94.5
8 | switch plate (2module) | each | 1.5 | 150 | 30% | 105 |  |  |  |  | 105 | 157.5
9 | 6A switch (Legrand make 01 module) | each | 1 | 140 | 30% | 98 |  |  |  |  | 98 | 98
10 | PVC fastener 40mm long | each | 3 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 2.1
11 | Cement, paint, sand etc. | each | 3 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 9.45
| Total | [10 empty] | 1217.3788
12 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 24.3476
1241.7264
13 | Installation,Testing and commissioning charges |  | 1 |  |  | 881.6 |  | 881.6 |  | 0 | 881.6 | 881.6
| WIREMAN G-1 | day | 0.6 | 579 |  | 347.4
| MASON G-2 | day | 0.2 | 579 |  | 115.8
| KHALLASI | day | 0.8 | 523 |  | 418.4
881.6
2123.3264
14 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 21.2333
2144.5596
15 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 321.6839
2466.2436
16 | Add 1% for WCT | [7 empty] | 1% |  |  | 24.6624
2490.906
17 | Service Tax 6% | [7 empty] | 6% |  |  | 149.4544
2640.3604
Rate per each
2640
| Say | [10 empty] | 2640
Rate Analysis for Item no.
Analysis for 1 point
d) 2way Light point 1Light with 2Nos 2 way switches
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 1.5sq.mm Copper wire (2runs) LP 1330/ 90MTS | mtr | 13.15 | 14.7778 | 30% | 10.3444 |  |  |  | 0 | 10.3444 | 136.0294
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%)
= 13.15m
2 | Heavy Guage 25mm dia PVC Conduit | mtr | 4.73 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 109.6156
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
3 | 25mm dia PVC Bends | each | 1 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 6.5048
4 | 25mm PVC couplers | each | 2 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 0.441
5 | 25 mm iron staples/ saddles/ screws | each | 9 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 13.23
6 | 25mm dia PVC Junction boxes one way | each | 1 | 26.47 | 30% | 18.529 |  |  | 5% | 0.92645 | 19.4554 | 19.4554
7 | 25mm dia PVC Junction boxes two way | each | 2 | 26.47 | 30% | 18.529 |  |  | 5% | 0.92645 | 19.4554 | 38.9109
8 | Metal box (2module) | each | 0.5 | 90 | 30% | 63 |  |  |  |  | 63 | 31.5
9 | switch plate (2module) | each | 0.5 | 150 | 30% | 105 |  |  |  |  | 105 | 52.5
10 | 6A switch (Legrand make 01 module) | each | 1 | 140 | 30% | 98 |  |  |  |  | 98 | 98
11 | PVC fastener 40mm long | each | 1 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 0.7
12 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 510.0372
13 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 10.2007
520.2379
14 | Installation,Testing and commissioning charges |  | 1 |  |  | 440.8 |  | 440.8 |  | 0 | 440.8 | 440.8
| WIREMAN G-1 | day | 0.3 | 579 |  | 173.7
| MASON G-2 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.4 | 523 |  | 209.2
440.8
961.0379
15 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 9.6104
970.6483
16 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 145.5972
1116.2455
17 | Add 1% for WCT | [7 empty] | 1% |  |  | 11.1625
1127.408
18 | Service Tax 6% | [7 empty] | 6% |  |  | 67.6445
1195.0525
Rate per each
1195
| Say | [10 empty] | 1195
e) Ceiling fan point with 1switch & Electronic regulator(Analysis for1 points)
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 1.5sq.mm Copper wire (2runs) LP 1330/ 90MTS | mtr | 13.15 | 14.7778 | 30% | 10.3444 |  |  |  | 0 | 10.3444 | 136.0294
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%)
= 13.15m
2 | Heavy Guage 25mm dia PVC Conduit | mtr | 4.73 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 109.6156
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
3 | 25mm dia PVC Bends | each | 1 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 6.5048
4 | 25mm PVC couplers | each | 2 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 0.441
5 | 25 mm iron staples/ saddles/ screws | each | 9 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 13.23
6 | 25mm dia PVC Junction boxes | each | 1 | 26.47 | 30% | 18.529 |  |  | 5% | 0.92645 | 19.4554 | 19.4554
7 | Metal box (3 module) | each | 0.5 | 90 | 30% | 63 |  |  |  |  | 63 | 31.5
8 | switch plate (3 module) | each | 0.5 | 150 | 30% | 105 |  |  |  |  | 105 | 52.5
9 | 6A switch (Legrand make 01 module) | each | 1 | 140 | 30% | 98 |  |  |  |  | 98 | 98
10 | PVC fastener 40mm long | each | 1 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 0.7
11 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
13 | 100 W Electronic regulator | each | 1 | 798 | 30% | 558.6 |  |  |  |  | 558.6 | 558.6
| Total | [10 empty] | 1029.7263
14 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 20.5945
1050.3208
15 | Installation,Testing and commissioning charges |  | 1 |  |  | 440.8 |  | 440.8 |  | 0 | 440.8 | 440.8
| WIREMAN G-1 | day | 0.3 | 579 |  | 173.7
| MASON G-2 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.4 | 523 |  | 209.2
440.8
1491.1208
16 | Add 1% for Electricity Charges |  | S | [5 empty] | 1% |  |  | 14.9112
1506.032
17 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 225.9048
1731.9368
18 | Add 1% for WCT | [7 empty] | 1% |  |  | 17.3194
1749.2562
19 | Service Tax 6% | [7 empty] | 6% |  |  | 104.9554
1854.2115
Rate per each
1854
| Say | [10 empty] | 1854
Rate Analysis for Item no.
(Analysis for 1 Number)
h) Supply and fixing of 6A, 5 Pin Socket outlet with switch of 6A rating in boards .
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 6A switch (01 module) | each | 1 | 140 | 30% | 98 |  |  |  |  | 98 | 98
2 | 6A 5Pin socket | each | 1 | 260 | 30% | 182 |  |  |  |  | 182 | 182
3 | MS box (3 module) | each | 1 | 90 | 30% | 63 |  |  |  |  | 63 | 63
4 | Switch Plate (3module) | each | 1 | 164 | 30% | 114.8 |  |  |  |  | 114.8 | 114.8
5 | PVC fastener 40mm long | each | 1 | 2 | 30% | 1.4 |  |  |  |  | 1.4 | 1.4
6 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 462.35
7 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 9.247
471.597
8 | Installation,Testing and commissioning charges |  | 1 |  |  | 125.14 |  | 125.14 |  | 0 | 125.14 | 125.14
| WIREMAN G-1 | day | 0.07 | 579 |  | 40.53 | [5 empty] | 596.737
| KHALLASI | day | 0.04 | 523 |  | 20.92
| MASON G-2 | day | 0.11 | 579 |  | 63.69
125.14
596.737
9 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 5.9674
602.7044
10 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 90.4057
693.11
11 | Add 1% for WCT | [7 empty] | 1% |  |  | 6.9311
700.0411
12 | Service Tax 6% | [7 empty] | 6% |  |  | 42.0025
742.0436
Rate per each
742
| Say | [10 empty] | 742
Rate Analysis for Item no.
IE-4 | Supply and Wiring with the following size 1.1KV grade FRLS PVC insulated Copper conductor multi strand wires in heavy duty PVC conduit concealed in wall / ceiling/above false ceiling , including junction boxes, bends, elbows including and terminated with suitable lugs.
a) Run of mains : 2R X 2.5 sq.mm with 1R x 1.5Sq.mm PVC conduit
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
(Analysis for 50 Mtr)
1 | 2.5sq.mm copper circuit wires(2runs) LP 2120/90 m | mtr | 106.05 | 23.56 | 30% | 16.492 |  |  | 5% | 0.8246 | 17.3166 | 1836.4254
= 50.5x2=101+5.05 (Wastage@ 5%)
=106.05m
2 | 1.5sq.mm copper circuit wires(1runs) LP 1330/90 m | mtr | 53.02 | 14.78 | 30% | 10.346 |  |  | 5% | 0.5173 | 10.8633 | 575.9722
= 50.5x1=50.5+2.52 (Wastage@ 5%)
=53.02m
3 | Heavy Guage 25mm dia Conduit | mtr | 52.5 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 1216.6639
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
4 | 25mm dia PVC Couplers | each | 15 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 3.3075
5 | 25mm dia PVC Bends | each | 4 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 26.019
6 | 25 mm iron staples/ saddles/ screws | each | 85 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 124.95
7 | PVC fastener 40mm long | each | 85 | 2 | 30% | 1.4 |  |  |  |  | 1.4 | 119
8 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 3905.488
9 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 78.1098
3983.5977
10 | Installation,Testing and commissioning charges |  | 50 |  |  | 60.61 |  | 60.61 |  | 0 | 60.61 | 3030.5
| WIREMAN G-1 | day | 2 | 579 |  | 1158
| MASON G-2 | day | 0.75 | 579 |  | 434.25
| KHALLASI | day | 2.75 | 523 |  | 1438.25
3030.5
7014.0977
11 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 70.141
7084.2387
12 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 1062.6358
8146.8745
13 | Add 1% for WCT | [7 empty] | 1% |  |  | 81.4687
8228.3433
14 | Service Tax 6% | [7 empty] | 6% |  |  | 493.7006
8722.0439
| Rate per each | [10 empty] | 174
| Say | [10 empty] | 174
Rate Analysis for Item no.
b) 4 runs of 6 Sq.mm wires with 2 run of 4 Sq.mm wire in 32 mm Dia PVC conduit.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
(Analysis for 50 Mtr)
1 | 6 sq.mm copper circuit wires(2runs) LP 2120/90 m | mtr | 212.1 | 52.8333 | 30% | 36.9833 |  |  | 5% | 1.8492 | 38.8325 | 8236.3733
50.5x4=202+ 10.1(Wastage @ 5%)=212.1m
2 | 4 sq.mm copper circuit wires(1runs) LP 1330/90 m | mtr | 106.05 | 34.2222 | 30% | 23.9556 |  |  | 5% | 1.1978 | 25.1533 | 2667.511
= 50.5x2=101+5.05 (Wastage@ 5%)
=106.05m
3 | Heavy Guage 25mm dia Conduit | mtr | 52.5 | 50.14 | 30% | 35.098 |  |  | 5% | 1.7549 | 36.8529 | 1934.7772
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
4 | 32mm dia PVC Couplers | each | 15 | 0.457 | 30% | 0.3199 |  |  | 5% | 0.015995 | 0.33589 | 5.0384
5 | 32mm dia PVC Bends | each | 4 | 19.38 | 30% | 13.566 |  |  | 5% | 0.6783 | 14.2443 | 56.9772
6 | 32mm iron staples/ saddles/ screws | each | 85 | 3.34 | 30% | 2.338 |  |  | 5% | 0.1169 | 2.4549 | 208.6665
7 | PVC fastener 40mm long | each | 85 | 2 | 30% | 1.4 |  |  |  |  | 1.4 | 119
8 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 13231.4936
9 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 264.6299
13496.1235
10 | Installation,Testing and commissioning charges |  | 50 |  |  | 66.12 |  | 66.12 |  | 0 | 66.12 | 3306
| WIREMAN G-1 | day | 2.25 | 579 |  | 1302.75
| MASON G-2 | day | 0.75 | 579 |  | 434.25
| KHALLASI | day | 3 | 523 |  | 1569
3306
16802.1235
11 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 168.0212
16970.1447
12 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 2545.5217
19515.6664
13 | Add 1% for WCT | [7 empty] | 1% |  |  | 195.1567
19710.8231
14 | Service Tax 6% | [7 empty] | 6% |  |  | 1182.6494
20893.4725
| Rate per each | [10 empty] | 418
| Say | [10 empty] | 418
MV Cables
Supply, laying and commissioning of following size 1.1KVgrade XLPE insulated armoured aluminium/ copper conductor underground cable, in built up cable trench/ already laid RCChume pipe or on cable tray with all installation materials..
Rate Analysis for Item no.
a) 3 core X 4 Sq mm copper flexible cable
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 3 core X 4 Sq mm copper flexible cable | mtr | 100 | 142.7 | 50% | 71.35 |  | 71.35 | 5% | 3.5675 | 74.9175 | 7491.75
| Gl saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 | 30% | 0.595 |  |  |  |  | 0.595 | 134.47
= 100/0.45 = 222 + 4 (Wastage @ 2%)
= 226 Nos
| Iron screws, 45 mm X 6 mm | each | 452 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 316.4
| Cement, paint, sand etc | each | 2 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 6.3
7948.92
| Total | [7 empty] | 2% |  |  | 158.9784
2 | Transportation, packing and forwarding charges | [10 empty] | 8107.8984
3 | Installation,Testing and commissioning charges |  | 100 |  |  | 13.5417 |  | 13.5417 |  | 0 | 13.5417 | 1354.1667
| WIREMAN G-1 | day | 1 | 579 |  | 579
| KHALLASI | day | 2 | 523 |  | 1046
9462.0651
4 | Electricity charges 1% | [7 empty] | 1% |  |  | 94.6207
9556.6857
5 | Contractor Overheads and Profits 15% | [7 empty] | 15% |  |  | 1433.5029
10990
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 109.9
11099.9
6 | Service Tax 6% | [7 empty] | 6% |  |  | 659.4
10997
| SAY | [10 empty] | 109.97
Rate Analysis for Item no.
b) 4C X 10 Sq.mm Aluminium
Rate Analysis for Item no.
b) 4C X 10 Sq.mm Aluminium
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | b) 4C X 10 Sq.mm Aluminium | mtr | 100 | 83.1 | 50% | 41.55 |  | 41.55 | 5% | 2.0775 | 43.6275 | 4362.75
| Gl saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 |  | 0.85 |  |  |  |  | 0.85 | 192.1
= 100/0.45 = 222 + 4 (Wastage @ 2%)
= 226 Nos
| Iron screws, 45 mm X 6 mm | each | 452 | 1 |  | 1 |  |  |  |  | 1 | 452
| Cement, paint, sand etc | each | 2 | 4.5 |  | 4.5 |  |  |  |  | 4.5 | 9
5015.85
| Total | [7 empty] | 2% |  |  | 100.317
2 | Transportation, packing and forwarding charges | [10 empty] | 5116.167
3 | Installation,Testing and commissioning charges |  | 100 |  |  | 16.25 |  | 16.25 |  |  | 16.25 | 1625
| WIREMAN G-1 | day | 1 | 579 |  | 579
| KHALLASI | day | 2 | 523 |  | 1046
6741.167
4 | Electricity charges 1% | [7 empty] | 1% |  |  | 67.4117
6808.5787
5 | Contractor Overheads and Profits 15% | [7 empty] | 15% |  |  | 1021.2868
7830
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 78.3
7908.3
6 | Service Tax 6% | [7 empty] | 6% |  |  | 469.8
7835
| SAY | [10 empty] | 78.35
ii) Providing Indoor ordinary end terminations for the cable specified above with compression type steel gland,Bi-metallic lugs using crimping tool,Insulation tape,Identification tags etc., including end termination.
Rate Analysis for Item no.
a) 3C X4 Sq.mm
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3C 4 sqmm GLANDS |  | 1 | 174.1 | 20% | 139.28 |  | 139.28 | 14.5% | 20.1956 | 159.4756 | 159.4756
2 | 4 sqmm LUG |  | 1 | 6.27 | 20% | 5.016 |  | 5.016 | 14.5% | 0.72732 | 5.7433 | 5.7433
3 | 4 sqmm LUG |  | 3 | 6.27 | 20% | 5.016 |  | 5.016 | 14.5% | 0.72732 | 5.7433 | 17.23
| Total | [10 empty] | 182.4489
4 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 3.649
186.0979
5 | Installation,Testing and commissioning charges |  | 1 |  |  | 110.2 |  | 110.2 |  |  | 110.2 | 110.2
| WIREMAN G-1 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.1 | 523 |  | 52.3
296.2979
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 2.963
299.2608
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 44.8891
344.15
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 3.4415
347.5915
8 | Service Tax 6% | [7 empty] | 6% |  |  | 20.8555
368.4469
368
Rate Analysis for Item no.
b) 4C X10 Sq.mm
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5 C 10 sqmm GLANDS |  | 1 | 289.6 | 20% | 231.68 |  | 231.68 | 14.5% | 33.5936 | 265.2736 | 265.2736
2 | 10sqmm LUG |  | 1 | 3.01 | 20% | 2.408 |  | 2.408 | 14.5% | 0.34916 | 2.7572 | 2.7572
3 | 10 sqmm LUG |  | 3 | 3.01 | 20% | 2.408 |  | 2.408 | 14.5% | 0.34916 | 2.7572 | 8.2715
| Total | [10 empty] | 276.3022
4 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 5.526
281.8283
5 | Installation,Testing and commissioning charges |  | 1 |  |  | 110.2 |  | 110.2 |  | 0 | 110.2 | 110.2
| WIREMAN G-1 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.1 | 523 |  | 52.3 | [5 empty] | 392.0283
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 3.9203
395.9486
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 59.3923
455.3409
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 4.5534
459.8943
8 | Service Tax 6% | [7 empty] | 6% |  |  | 27.5937
487.4879
487
Supply, installing, testing and commissioning of Powder coated G.I cable tray of perforated type 100mm wide with GI cover (both 2mm thick) including suitable powder coated MS supports etc. complete as per the specifications and approved drawings.
Rate Analysis for Item no.
100mm X 50 mm X 1.6 mm thickness.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 100mm X 50 mm X 1.6 mm thickness. |  | 1 | 459 | 30% | 321.3 | 14% | 366.282 | 5% | 16.065 | 382.347 | 382.347
| Total | [10 empty] | 382.347
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 7.6469
389.9939
3 | Installation,Testing and commissioning charges |  | 1 |  |  | 186.78 |  | 186.78 |  | 0 | 186.78 | 186.78
| Fitter grade-2 | day | 2 | 579 |  | 1158
| MASON G-2 | day | 2 | 579 |  | 1158
| KHALLASI | day | 4.5 | 523 |  | 2353.5
576.7739
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 5.7677
582.5417
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 87.3813
670
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 6.7
676.7
7 | Service Tax 6% | [7 empty] | 6% |  |  | 40.2
710
710
LIGHT / FAN FIXTURES
Rate Analysis for Item no.
a) 33W Recess Mounted 2ft x 2ft LED Luminaire with Diffuser similar to CAT NO: CRCO10R036HP57G1, WIPRO MAKE
(Analysis for 1 Number)
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | a) 33W Recess Mounted 2ft x 2ft LED Luminaire with Diffuser similar to CAT NO: CRCO10R036HP57G1, WIPRO MAKE |  | 1 | 6190 | 30% | 4333 |  | 4333 |  |  | 4333 | 4333
| Total | [10 empty] | 4333
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 86.66
4419.66
3 | Installation,Testing and commissioning charges |  | 1 |  |  | 585.712 |  | 585.712 |  | 0 | 585.712 | 585.712
a | 1.5 Sq.mm ISI Marked. FR PVC insulated single core copper conductor | mtr | 0.9 | 14.78 |  | 13.302
b | 20mm dia.ISI Marked,steel conduit | mtr | 0.6 | 127 |  | 76.2
c | Iron screws, 35mm X 6mm | Each | 6 | 36 |  | 216
d | Washers | Each | 2 | 11 |  | 22
e | Rubber or PVC bushes | Each | 1 | 45 |  | 45
f | WIREMAN G-1 | day | 0.165 | 579 |  | 95.535
g | KHALLASI | day | 0.165 | 523 |  | 86.295
h | Painter | day | 0.06 | 523 |  | 31.38
5005.372
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 50.0537
5055.4257
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 758.3139
5813.7396
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 58.1374
5871.877
7 | Service Tax 6% | [7 empty] | 6% |  |  | 352.3126
6224.1896
| Rate per each | [10 empty] | 6224
| Say | [10 empty] | 6224
Rate Analysis for Item no.
b) 12W Recess mounted circular LED downlighter ( CAT NO: CRDL11R017HP57 WIPRO MAKE
(Analysis for 1 Number)
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 12W Recess mounted circular LED downlighter ( CAT NO: CRDL11R017HP57 WIPRO MAKE | Each | 1 | 2250 | 30% | 1575 |  |  | 14.5% | 228.375 | 1803.375 | 1803.375
| Total | [10 empty] | #NUM!
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | #NUM!
#NUM!
3 | Installation,Testing and commissioning charges |  | 1 |  |  | 281.184 |  | 281.184 |  | 0 | 281.184 | 281.184
a | 1.5 Sq.mm ISI Marked. FR PVC insulated single core copper conductor | mtr | 0.3 | 14.78 |  | 4.434
b | Iron screws, 35mm X 6mm | Each | 2 | 36 |  | 72
c | Washers | Each | 2 | 11 |  | 22
d | Rubber or PVC bushes | Each | 1 | 45 |  | 45
e | WIREMAN G-1 | day | 0.125 | 579 |  | 72.375
f | KHALLASI | day | 0.125 | 523 |  | 65.375
2377.604
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 23.776
2401.38
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 360.207
2761.587
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 27.6159
2789.2029
7 | Service Tax 6% | [7 empty] | 6% |  |  | 167.3522
2956.5551
| Rate per each | [10 empty] | 2957
| Say | [10 empty] | 2957
Rate Analysis for Item no.
a) 139.2 W Radial Prime LED Highbay similar CAT NO. LH09-172- 060-50-G1 WIPRO MAKE
(Analysis for 1 Number)
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | a) 139.2 W Radial Prime LED Highbay similar CAT NO. LH09-172- 060-50-G1 WIPRO MAKE |  | 1 | 27550 | 30% | 19285 |  | 19285 |  |  | 19285 | 19285
| Total | [10 empty] | 19285
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 385.7
19670.7
3 | Installation,Testing and commissioning charges |  | 1 |  |  | 281.184 |  | 281.184 |  | 0 | 281.184 | 281.184
a | 1.5 Sq.mm ISI Marked. FR PVC insulated single core copper conductor | mtr | 0.3 | 14.78 |  | 4.434
b | Iron screws, 35mm X 6mm | Each | 2 | 36 |  | 72
c | Washers | Each | 2 | 11 |  | 22
d | Rubber or PVC bushes | Each | 1 | 45 |  | 45
e | WIREMAN G-1 | day | 0.125 | 579 |  | 72.375
f | KHALLASI | day | 0.125 | 523 |  | 65.375
19951.884
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 199.5188
20151.4028
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 3022.7104
23174.1133
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 231.7411
23405.8544
7 | Service Tax 6% | [7 empty] | 6% |  |  | 1404.3513
24810.2057
| Rate per each | [10 empty] | 24810
| Say | [10 empty] | 24810
Rate Analysis for Item no.
Ceiling Fans
Supply &Fixing of 1200 mm sweep Ceiling fan with standard down rod, all accessories Electrical connections. Including fixing materials required.
(Analysis for 1 Number)
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 1200mm Ceiling Fan |  | 1 | 2275 | 20% | 1820 |  | 1820 |  |  | 1820 | 1820
| Total | [10 empty] | 1820
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 36.4
1856.4
3 | Installation,Testing and commissioning charges |  | 1 |  |  | 137.75 |  | 137.75 |  | 0 | 137.75 | 137.75
| WIREMAN G-1 | day | 1 | 579 |  | 579
| KHALLASI | day | 1 | 523 |  | 523
1102
1994.15
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 19.9415
2014.0915
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 302.1137
2316.2052
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 23.1621
2339.3673
7 | Service Tax 6% | [7 empty] | 6% |  |  | 140.362
2479.7293
| Rate per each | [10 empty] | 2480
| Say | [10 empty] | 2480
Rate Analysis for Item no.
Exhaust Fans
Supply and Installation of heavy duty Exhaust fans with Metallic blades following size sweep with gravity louvres shutters Exhaust fans with Metallic blades of following
(Analysis for 1 Number)
a) 300mm Sweep Metal Body
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 300mm Sweep Metal Body |  | 1 | 3615 | 20% | 2892 |  | 2892 |  |  | 2892 | 2892
| Total | [10 empty] | 2892
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 57.84
2949.84
3 | Installation,Testing and commissioning charges |  | 1 |  |  | 727.32 |  | 727.32 |  | 0 | 727.32 | 727.32
| WIREMAN G-1 | day | 0.33 | 579 |  | 191.07
| Mason G-2 | day | 0.33 | 579 |  | 191.07
| KHALLASI | day | 0.66 | 523 |  | 345.18
727.32
3677.16
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 36.7716
3713.9316
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 557.0897
4271.0213
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 42.7102
4313.7316
7 | Service Tax 6% | [7 empty] | 6% |  |  | 258.8239
4572.5554
| Rate per each | [10 empty] | 4573
| Say | [10 empty] | 4573
Rate Analysis for Item no.
6 Amps, 5-pin (250 Volts) single phase commercial type socket controlled by 6 Amps SP Switch . The pin configuration shall be round type. (Independent type) with 2runs of 1.1 kV grade FRLS PVC 1.5 Sq.mm & 1 run of 1.5 Sq.mm multi strand Copper wires , run in and including 25 mm dia Heavy duty PVC conduits concealed in wall / ceiling/above false ceiling conforming to IS including all accessories such as junction boxes, conduit bends elbows.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 1.5sq.mm Copper wire (2runs) LP 1330/ 90MTS | mtr | 13.15 | 14.78 | 30% | 10.346 |  |  |  | 0 | 10.346 | 136.0499
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%)
= 13.15m
2 | Heavy Guage 25mm dia PVC Conduit | mtr | 4.73 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 109.6156
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
3 | 25mm dia PVC Bends | each | 1 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 6.5048
4 | 25mm PVC couplers | each | 2 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 0.441
5 | 25 mm iron staples/ saddles/ screws | each | 9 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 13.23
6 | 25mm dia PVC Junction boxes | each | 1 | 26.47 | 30% | 18.529 |  |  | 5% | 0.92645 | 19.4554 | 19.4554
7 | Metal box (3module) | each | 1 | 90 | 30% | 63 |  |  |  |  | 63 | 63
8 | switch plate (3module) | each | 1 | 164 | 30% | 114.8 |  |  |  |  | 114.8 | 114.8
9 | 6A switch (Legrand make 01 module) | each | 1 | 140 | 30% | 98 |  |  |  |  | 98 | 98
10 | 6A 5Pin socket | each | 1 | 260 | 30% | 182 |  |  |  |  | 182 | 182
11 | PVC fastener 40mm long | each | 1 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 0.7
12 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 746.9467
13 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 14.9389
761.8857
14 | Installation,Testing and commissioning charges |  | 1 |  |  | 562.02 |  | 562.02 |  | 0 | 562.02 | 562.02
| WIREMAN G-1 | day | 0.37 | 579 |  | 214.23
| MASON G-2 | day | 0.14 | 579 |  | 81.06
| KHALLASI | day | 0.51 | 523 |  | 266.73
562.02
1323.9057
15 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 13.2391
1337.1447
16 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 200.5717
1537.7164
17 | Add 1% for WCT | [7 empty] | 1% |  |  | 15.3772
1553.0936
18 | Service Tax 6% | [7 empty] | 6% |  |  | 93.1856
1646.2792
Rate per each
1646
| Say | [10 empty] | 1646
Rate Analysis for Item no.
Supply Installation Testing and commissioning of TPN MCB Double door Distribution boards dust and vermin protected and rated for 415V Three Phase AC supply operation including incoming MCB /ELCB as per specifications and required capacity Neutral bar and Earth terminal complete as required and installed in flush with wall including all fixing materials required. MCBs shall conform to IS : 8828 and ELCB /RCCB shall conform to IS : 12640
4Way TPN MCB DB( Horizontal type)with 40A, 4Pole RCBO, 100mA sensitivity as incomer and 12 nos 6-32A SPMCBs s outgoings
(Analysis for 1 Number)
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 4WAY TPN MCB DB IP 43 LEGRAND double door |  | 1 | 5526 | 30% | 3868.2 |  | 3868.2 |  | 0 | 3868.2 | 3868.2
2 | 40A FP RCBO, 100mA |  | 1 | 5758 | 30% | 4030.6 |  | 4030.6 |  |  | 4030.6 | 4030.6
3 | 6-32 A SP MCB |  | 12 | 294 | 30% | 205.8 |  | 205.8 |  |  | 205.8 | 2469.6
4 | Steel fastener 6 mm X 75 mm |  | 4 | 5 |  | 5 |  | 5 |  |  | 5 | 20
5 | Cement, paint, sand etc |  | 1 | 4.5 |  | 4.5 |  | 4.5 |  |  | 4.5 | 4.5
| Total | [10 empty] | 10392.9
6 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 207.858
10600.758
7 | Installation,Testing and commissioning charges |  | 1 |  |  | 881.6 |  | 881.6 |  | 0 | 881.6 | 881.6
| WIREMAN G-1 | day | 0.68 | 579 |  | 393.72
| MASON G-2 | day | 0.12 | 579 |  | 69.48
| KHALLASI | day | 0.8 | 523 |  | 418.4
11482.358
8 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 114.8236
11597.1816
9 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 1739.5772
13336.7588
10 | Add 1% for WCT | [7 empty] | 1% |  |  | 133.3676
13470.1264
11 | Service Tax 6% | [7 empty] | 6% |  |  | 808.2076
14278.334
| Rate per each | [10 empty] | 14278
| Say | [10 empty] | 14278
SUB HEAD - 2 : POWER WIRING
Rate Analysis for Item no.
Supply Installation Testing and commissioning of TPN MCB Double door Distribution boards dust and vermin protected and rated for 415V Three Phase AC supply operation including incoming MCB /ELCB as per specifications and required capacity Neutral bar and Earth terminal complete as required and installed in flush with wall including all fixing materials required. MCBs shall conform : 8828 and ELCB /RCCB shall conform to IS : 12640
a)Way VTPN MCB DB( Vertical type)with 63A, 4Pole MCB as incomer and 2 nos 32 A TP MCBs and 6nos 6-32A SPMCBs s outgoings(PDB's).
(Analysis for 1 Number)
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 4WAY V TPN MCB DB IP 43 LEGRAND |  | 1 | 10482 | 30% | 7337.4 |  | 7337.4 |  |  | 7337.4 | 7337.4
2 | 63A FP MCB, |  | 1 | 2774 | 30% | 1941.8 |  | 1941.8 |  |  | 1941.8 | 1941.8
3 | 32 A TP MCB |  | 2 | 1422 | 30% | 995.4 |  | 995.4 |  |  | 995.4 | 1990.8
4 | 6-32 A SP MCB |  | 6 | 294 | 30% | 205.8 |  | 205.8 |  |  | 205.8 | 1234.8
5 | Steel fastener 6 mm X 75 mm |  | 4 | 5 |  | 5 |  | 5 |  |  | 5 | 20
6 | Cement, paint, sand etc |  | 1 | 4.5 |  | 4.5 |  | 4.5 |  |  | 4.5 | 4.5
| Total | [10 empty] | 12529.3
7 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 250.586
12779.886
8 | Installation,Testing and commissioning charges |  | 1 |  |  | 946.41 |  | 946.41 |  | 0 | 946.41 | 946.41
| WIREMAN G-1 | day | 0.78 | 579 |  | 451.62
| MASON G-2 | day | 0.15 | 579 |  | 86.85
| KHALLASI | day | 0.78 | 523 |  | 407.94
13726.296
9 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 137.263
13863.559
10 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 2079.5338
15943.0928
11 | Add 1% for WCT | [7 empty] | 1% |  |  | 159.4309
16102.5237
12 | Service Tax 6% | [7 empty] | 6% |  |  | 966.1514
17068.6752
| Rate per each | [10 empty] | 17069
| Say | [10 empty] | 17069
Rate Analysis for Item no.
Supply Installation Testing and commissioning of TPN MCB Double door Distribution boards dust and vermin protected and rated for 415V Three Phase AC supply operation including incoming MCB /ELCB as per specifications and required capacity Neutral bar and Earth terminal complete as required and installed in flush with wall including all fixing materials required. MCBs shall conform : 8828 and ELCB /RCCB shall conform to IS : 12640
a)4Way TPN MCB DB with 63A, 4Pole MCB as incomer and 12nos 6-32A SPMCBs s outgoings(PDB's).
(Analysis for 1 Number)
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 4WAY TPN MCB DB IP 43 LEGRAND |  | 1 | 5526 | 30% | 3868.2 |  | 3868.2 |  | 0 | 3868.2 | 3868.2
2 | 63A FP MCB, |  | 1 | 2774 | 30% | 1941.8 |  | 1941.8 |  |  | 1941.8 | 1941.8
3 | 6-32 A SP MCB |  | 12 | 294 | 30% | 205.8 |  | 205.8 |  |  | 205.8 | 2469.6
4 | Steel fastener 6 mm X 75 mm |  | 4 | 5 |  | 5 |  | 5 |  |  | 5 | 20
5 | Cement, paint, sand etc |  | 1 | 4.5 |  | 4.5 |  | 4.5 |  |  | 4.5 | 4.5
| Total | [10 empty] | 8304.1
6 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 166.082
8470.182
7 | Installation,Testing and commissioning charges |  | 1 |  |  | 946.41 |  | 946.41 |  | 0 | 946.41 | 946.41
| WIREMAN G-1 | day | 0.78 | 579 |  | 451.62
| MASON G-2 | day | 0.15 | 579 |  | 86.85
| KHALLASI | day | 0.78 | 523 |  | 407.94
9416.592
8 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 94.1659
9510.7579
9 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 1426.6137
10937.3716
10 | Add 1% for WCT | [7 empty] | 1% |  |  | 109.3737
11046.7453
11 | Service Tax 6% | [7 empty] | 6% |  |  | 662.8047
11709.55
| Rate per each | [10 empty] | 11710
| Say | [10 empty] | 11710
DOMESTIC TYPE MODULAR AND INDUSTRIAL SOCKETS
Rate Analysis for Item no.PW-1.1
a) 16/6 Amps, (250 Volts) single phase commercial type socket controlled by 16 Amps SP Switch . The pin configuration shall be round type. (Independent type)
(Analysis for 1 Number)
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 16 A/ 6 A SOCKET , LEGRAND 3 module |  | 1 | 358 | 30% | 250.6 |  | 250.6 |  |  | 250.6 | 250.6
2 | 16 A SWITCH, LEGRAND |  | 1 | 244 | 30% | 170.8 |  | 170.8 |  |  | 170.8 | 170.8
3 | 4 MODULE BOX |  | 1 | 90 | 30% | 63 |  | 63 |  |  | 63 | 63
4 | 4 MODULE FRONT PLATE |  | 1 | 164 | 30% | 114.8 |  | 114.8 |  |  | 114.8 | 114.8
| Total | [10 empty] | 599.2
5 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 11.984
611.184
6 | Installation,Testing and commissioning charges |  | 1 |  |  | 66.12 |  | 66.12 |  | 0 | 66.12 | 66.12
| WIREMAN G-1 | day | 0.06 | 579 |  | 34.74
| KHALLASI | day | 0.06 | 523 |  | 31.38
66.12
677.304
7 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 6.773
684.077
8 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 102.6116
786.6886
9 | Add 1% for WCT | [7 empty] | 1% |  |  | 7.8669
794.5555
10 | Service Tax 6% | [7 empty] | 6% |  |  | 47.6733
842.2288
| Rate per each | [10 empty] | 842
| Say | [10 empty] | 842
Supply and fixing of factory made 25A Single phase socket with 25A SPMCB in MS box including all fixing accessories.( for 1.5Tr & 2 Tr ACs )
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 25A Metal clad Socket point | each | 1 | 2012 | 30% | 1408.4 |  |  |  |  | 1408.4 | 1408.4
2 | 25A SP MCB | each | 1 | 294 | 30% | 205.8 |  |  |  |  | 205.8 | 205.8
3 | Steel fastener 6 mm X 75 mm |  | 4 | 5 |  | 5 |  | 5 |  |  | 5 | 20
4 | Cement, paint, sand etc |  | 1 | 4.5 |  | 4.5 |  | 4.5 |  |  | 4.5 | 4.5
| Total | [10 empty] | 1638.7
| Transportation | [9 empty] | 2% | 32.774
5 | Labour charges
| Wireman | Day | 0.18 | 579 | [7 empty] | 104.22
| Khallasi | Day | 0.15 | 523 | [7 empty] | 78.45
| MASON G-2 | Day | 0.18 | 579 | [7 empty] | 104.22
| Total | [10 empty] | 1958.364
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 19.5836
1977.9476
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 296.6921
2274.6398
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 22.7464
2297.3862
9 | Service Tax 6% | [7 empty] | 6% |  |  | 137.8432
2435.2294
| Rate per each | [10 empty] | 2435
| Say | [10 empty] | 2435
Rate Analysis for Item no.
c) Supply and fixing of factory made 32 A 3p+N+e Metalclad socket with 32A TP MCB in MS box including all fixing accessories.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 32 A METAL CLAD SOCKET WITH LEGRAND |  | 1 | 5580 | 30% | 3906 |  | 3906 |  | 0 | 3906 | 3906
2 | 32 A TP MCB, LEGRAND |  | 1 | 1422 | 30% | 995.4 |  | 995.4 |  | 0 | 995.4 | 995.4
3 | Steel fastener 6 mm X 75 mm |  | 4 | 5 |  | 5 |  | 5 |  |  | 5 | 20
4 | Cement, paint, sand etc |  | 1 | 4.5 |  | 4.5 |  | 4.5 |  |  | 4.5 | 4.5
| Total | [10 empty] | 4925.9
5 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 98.518
5024.418
6 | Installation,Testing and commissioning charges |  | 1 |  |  | 171.09 |  | 171.09 |  | 0 | 171.09 | 171.09
| WIREMAN G-1 | day | 0.08 | 579 |  | 46.32
| MASON G-2 | day | 0.08 | 579 |  | 46.32
| KHALLASI | day | 0.15 | 523 |  | 78.45
5195.508
7 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 51.9551
5247.4631
8 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 787.1195
6035
9 | Add 1% for WCT | [7 empty] | 1% |  |  | 60.35
6095.35
10 | Service Tax 5.80% | [7 empty] | 5.8% |  |  | 350.03
6385
| SAY | [10 empty] | 6385
Supply and Wiring with the following size 1.1KV grade FRLS PVC insulated Copper conductor wires& including in suitable size heavy duty PVC conduit concealed in wall / above false junction boxes, bends, elbows including junction boxes, bends, elbows including and terminated with suitable lugs.
Rate Analysis for Item no.
a) 2runs of 4Sq.mm wires with 1run of 2.5 Sq.mm wires in 25 mm dia conduit
(Analysis for 50 Mtr)
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
(Analysis for 50 Mtr)
1 | 4sq.mm copper circuit wires(2runs) LP 2120/90 m | mtr | 106.05 | 34.2222 | 30% | 23.9556 |  |  | 5% | 1.1978 | 25.1533 | 2667.511
= 50.5x2=101+5.05 (Wastage@ 5%)
=106.05m
2 | 2.5sq.mm copper circuit wires(1runs) LP 1330/90 m | mtr | 53.02 | 23.5556 | 30% | 16.4889 |  |  | 5% | 0.82444 | 17.3133 | 917.9529
= 50.5x1=50.5+2.52 (Wastage@ 5%)
=53.02m
3 | Heavy Guage 25mm dia Conduit | mtr | 52.5 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 1216.6639
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
4 | 25mm dia PVC Couplers | each | 15 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 3.3075
5 | 25mm dia PVC Bends | each | 4 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 26.019
6 | 25 mm iron staples/ saddles/ screws | each | 85 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 124.95
7 | PVC fastener 40mm long | each | 85 | 2 | 30% | 1.4 |  |  |  |  | 1.4 | 119
8 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 5078.5543
9 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 101.5711
5180.1254
10 | Installation,Testing and commissioning charges |  | 50 |  |  | 60.61 |  | 60.61 |  | 0 | 60.61 | 3030.5
| WIREMAN G-1 | day | 2 | 579 |  | 1158
| MASON G-2 | day | 0.75 | 579 |  | 434.25
| KHALLASI | day | 2.75 | 523 |  | 1438.25
3030.5
8210.6254
11 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 82.1063
8292.7316
12 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 1243.9097
9536.6414
13 | Add 1% for WCT | [7 empty] | 1% |  |  | 95.3664
9632.0078
14 | Service Tax 6% | [7 empty] | 6% |  |  | 577.9205
10209.9283
| Rate per each | [10 empty] | 204
| Say | [10 empty] | 204
Rate Analysis for Item no.
b) 2 runs of 6Sq.mm wires with 1 run of 4 Sq.mm wire in 25 mm Dia PVC conduit
(Analysis for 50 Mtr)
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
(Analysis for 50 Mtr)
1 | 6 sq.mm copper circuit wires(2runs) LP 2120/90 m | mtr | 106.05 | 52.8333 | 30% | 36.9833 |  |  | 5% | 1.8492 | 38.8325 | 4118.1866
50.5x2=101+ 5.05(Wastage @ 5%)=106.05m
2 | 4 sq.mm copper circuit wires(1runs) LP 1330/90 m | mtr | 53.02 | 34.2222 | 30% | 23.9556 |  |  | 5% | 1.1978 | 25.1533 | 1333.6297
= 50.5x1=50.5+2.52 (Wastage@ 5%)
=106.05m
3 | Heavy Guage 25mm dia Conduit | mtr | 52.5 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 1216.6639
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
4 | 25mm dia PVC Couplers | each | 15 | 0.3 | 30% | 0.21 |  |  | 5% | 0.0105 | 0.2205 | 3.3075
5 | 25mm dia PVC Bends | each | 4 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 26.019
6 | 25 mm iron staples/ saddles/ screws | each | 85 | 2 | 30% | 1.4 |  |  | 5% | 0.07 | 1.47 | 124.95
7 | PVC fastener 40mm long | each | 85 | 2 | 30% | 1.4 |  |  |  |  | 1.4 | 119
8 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 6944.9067
9 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 138.8981
7083.8049
10 | Installation,Testing and commissioning charges |  | 50 |  |  | 52.765 |  | 52.765 |  | 0 | 52.765 | 2638.25
| WIREMAN G-1 | day | 2 | 579 |  | 1158
| MASON G-2 | day | 0.75 | 579 |  | 434.25
| KHALLASI | day | 2 | 523 |  | 1046
2638.25
9722.0549
11 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 97.2205
9819.2754
12 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 1472.8913
11292.1667
13 | Add 1% for WCT | [7 empty] | 1% |  |  | 112.9217
11405.0884
14 | Service Tax 6% | [7 empty] | 6% |  |  | 684.3053
12089.3937
| Rate per each | [10 empty] | 242
Rate Analysis for Item no.
c) 4 runs of 10Sq.mm wires with 2 run of 6 Sq.mm wire in 40 mm Dia PVC conduit (PDBs)
(Analysis for 50 Mtr)
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
(Analysis for 50 Mtr)
1 | 10sq.mm copper circuit wires(2runs) LP 2120/90 m | mtr | 212.1 | 76.4 | 30% | 53.48 |  |  | 5% | 2.674 | 56.154 | 11910.2634
50.5x4=202+ 10.1(Wastage @ 5%)=212.1m
2 | 6 sq.mm copper circuit wires(1runs) LP 1330/90 m | mtr | 106.05 | 52.8333 | 30% | 36.9833 |  |  | 5% | 1.8492 | 38.8325 | 4118.1866
= 50.5x2=101+5.05 (Wastage@ 5%)
=106.05m
3 | Heavy Guage 40 mm dia Conduit | mtr | 52.5 | 66.88 | 30% | 46.816 |  |  | 5% | 2.3408 | 49.1568 | 2580.732
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
4 | 40 mm dia PVC Couplers | each | 15 | 7.35 | 30% | 5.145 |  |  | 5% | 0.25725 | 5.4022 | 81.0337
5 | 40mm dia PVC Bends | each | 4 | 28.75 | 30% | 20.125 |  |  | 5% | 1.0063 | 21.1313 | 84.525
6 | 40 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 30% | 2.338 |  |  | 5% | 0.1169 | 2.4549 | 208.6665
7 | PVC fastener 40mm long | each | 85 | 2 | 30% | 1.4 |  |  |  |  | 1.4 | 119
8 | Cement, paint, sand etc. | each | 1 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 3.15
| Total | [10 empty] | 19105.5573
9 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 382.1111
19487.6684
10 | Installation,Testing and commissioning charges |  | 50 |  |  | 71.63 |  | 71.63 |  | 0 | 71.63 | 3581.5
| WIREMAN G-1 | day | 2.5 | 579 |  | 1447.5
| MASON G-2 | day | 0.75 | 579 |  | 434.25
| KHALLASI | day | 3.25 | 523 |  | 1699.75
3581.5
23069.1684
11 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 230.6917
23299.8601
12 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 3494.979
26794.8391
13 | Add 1% for WCT | [7 empty] | 1% |  |  | 267.9484
27062.7875
14 | Service Tax 6% | [7 empty] | 6% |  |  | 1623.7673
28686.5548
| Rate per each | [10 empty] | 574
MV Cables
i) Supply, laying and commissioning of following size 1.1KVgrade XLPE insulated armoured aluminium/ copper conductor underground cable, in built up cable trench/ already laid RCChume pipe or on cable tray with all installation materials..
Rate Analysis for Item no.
a) 4C X 10 Sq.mm Aluminium
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 4C X 10 Sq.mm Aluminium | mtr | 100 | 83.1 | 50% | 41.55 |  | 41.55 | 5% | 2.0775 | 43.6275 | 4362.75
2 | Gl saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 |  | 0.85 |  |  |  |  | 0.85 | 192.1
3 | Iron screws, 45 mm X 6 mm | each | 452 | 1 |  | 1 |  |  |  |  | 1 | 452
4 | Cement, paint, sand etc | each | 2 | 4.5 |  | 4.5 |  |  |  |  | 4.5 | 9
5006.85
| Total | [7 empty] | 2% |  |  | 100.137
5 | Transportation, packing and forwarding charges | [10 empty] | 5106.987
6 | Installation,Testing and commissioning charges |  | 1 |  |  | 9.8667 |  | 9.8667 |  | 0 | 9.8667 | 9.8667
| WIREMAN G-1 | day | 1 | 448 |  | 448
| KHALLASI | day | 2 | 368 |  | 736
5116.8537
7 | Electricity charges 1% | [7 empty] | 1% |  |  | 51.1685
5168.0222
8 | Contractor Overheads and Profits 15% | [7 empty] | 15% |  |  | 775.2033
5943
9 | Add 1% for WCT | [7 empty] | 1% |  |  | 59.43
6002.43
10 | Service Tax 6% | [7 empty] | 6% |  |  | 360.1458
6362.5758
| SAY | [10 empty] | 63.63
Rate Analysis for Item no.
b) 4C X 16 Sq.mm Aluminium
S.NO | DESCRIPTION | UNIT | QTY. | LP | DIS | LP Rate | ED | ED Rate | Taxes | Taxes Rate | T.Rate | Amount
1 | 4C X 16 Sq.mm Aluminium | mtr | 100 | 116.8 | 50% | 58.4 |  | 58.4 | 5% | 2.92 | 61.32 | 6132
2 | Gl saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 |  | 0.85 |  |  |  |  | 0.85 | 192.1
3 | Iron screws, 45 mm X 6 mm | each | 452 | 1 |  | 1 |  |  |  |  | 1 | 452
4 | Cement, paint, sand etc | each | 2 | 4.5 |  | 4.5 |  |  |  |  | 4.5 | 9
6785.1
| Total | [7 empty] | 2% |  |  | 9.04
5 | Transportation, packing and forwarding charges | [10 empty] | 7255.14
6 | Installation,Testing and commissioning charges |  | 1 |  |  | 9.8667 |  | 9.8667 |  | 0 | 9.8667 | 9.8667
| WIREMAN G-1 | day | 1 | 448 |  | 448
| KHALLASI | day | 2 | 368 |  | 736
7265.0067
7 | Electricity charges 1% | [7 empty] | 1% |  |  | 72.6501
7337.6567
8 | Contractor Overheads and Profits 15% | [7 empty] | 15% |  |  | 1100.6485
8438
9 | Add 1% for WCT | [7 empty] | 1% |  |  | 84.38
8522.38
10 | Service Tax 6% | [7 empty] | 6% |  |  | 506.28
8944
| SAY | [10 empty] | 89.44
Providing Indoor ordinary end terminations for the cable specified above with compression type steel gland,Bi-metallic lugs using crimping tool,Insulation tape,Identification tags etc., including end termination.
Rate Analysis for Item no.
a) 4C X10 Sq.mm
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 4 C 10 sqmm GLANDS |  | 1 | 289.6 | 20% | 231.68 |  | 231.68 | 14.5% | 33.5936 | 265.2736 | 265.2736
2 | 10 sqmm LUG |  | 1 | 2.67 | 20% | 2.136 |  | 2.136 | 14.5% | 0.30972 | 2.4457 | 2.4457
3 | 10 sqmm LUG |  | 3 | 2.67 | 20% | 2.136 |  | 2.136 | 14.5% | 0.30972 | 2.4457 | 7.3372
| Total | [10 empty] | 275.0565
4 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 5.5011
280.5576
5 | Installation,Testing and commissioning charges |  | 1 |  |  | 110.2 |  | 110.2 |  |  | 110.2 | 110.2
| WIREMAN G-1 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.1 | 523 |  | 52.3
390.7576
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 3.9076
394.6652
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 59.1998
453.865
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 4.5386
458.4036
8 | Service Tax 6% | [7 empty] | 6% |  |  | 27.5042
485.9078
486
Rate Analysis for Item no.
b) 4C X16 Sq.mm
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 4 C 16 sqmm GLANDS |  | 1 | 289.6 | 20% | 231.68 |  | 231.68 | 14.5% | 33.5936 | 265.2736 | 265.2736
2 | 16 sqmm LUG |  | 1 | 3.01 | 20% | 2.408 |  | 2.408 | 14.5% | 0.34916 | 2.7572 | 2.7572
3 | 16 sqmm LUG |  | 3 | 3.01 | 20% | 2.408 |  | 2.408 | 14.5% | 0.34916 | 2.7572 | 8.2715
| Total | [10 empty] | 276.3022
4 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 5.526
281.8283
5 | Installation,Testing and commissioning charges |  | 1 |  |  | 110.2 |  | 110.2 |  |  | 110.2 | 110.2
| WIREMAN G-1 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.1 | 523 |  | 52.3
392.0283
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 3.9203
395.9486
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 59.3923
455.3409
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 4.5534
459.8943
8 | Service Tax 6% | [7 empty] | 6% |  |  | 27.5937
487.4879
487
Supply, installing, testing and commissioning of Powder coated G.I cable tray of perforated type 150mm wide with GI cover (both 2mm thick) including suitable powder coated MS supports etc. complete as per the specifications and approved drawings.
Rate Analysis for Item no.
150mm X 50 mm X 1.6 mm thickness.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 150mm X 50 mm X 1.6 mm thickness. |  | 1 | 523 | 30% | 366.1 | 14% | 417.354 | 5% | 18.305 | 435.659 | 435.659
| Total | [10 empty] | 435.659
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 8.7132
444.3722
3 | Installation,Testing and commissioning charges |  | 1 |  |  | 131.36 |  | 131.36 |  | 0 | 131.36 | 131.36
| Fitter grade-2 | day | 2 | 407 |  | 814
| MASON G-2 | day | 2 | 407 |  | 814
| KHALLASI | day | 4.5 | 368 |  | 1656
575.7322
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 5.7573
581.4895
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 87.2234
669
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 6.69
675.69
7 | Service Tax 5.80% | [7 empty] | 5.8% |  |  | 38.802
708
708
SUB HEAD - : TELEPHONE & LAN
Rate Analysis for Item no.
Supply and laying of 25mm dia. PVC conduit concealed in wall/ ceiling/floor including all accessories such as junction boxes, conduit bends, etc completed as required for Telephones etc.,
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | Heavy Guage 25mm dia Conduit | mtr | 52.5 | 31.53 | 30% | 22.071 |  |  | 5% | 1.1036 | 23.1745 | 1216.6639
2 | Couplers | each | 15 | 3.02 | 30% | 2.114 |  |  | 5% | 0.1057 | 2.2197 | 33.2955
3 | Bends & Elbows | each | 4 | 8.85 | 30% | 6.195 |  |  | 5% | 0.30975 | 6.5048 | 26.019
4 | 25 mm iron staples/ saddles/ screws | each | 85 | 2 |  | 2 |  |  |  | 0 | 2 | 170
5 | PVC fastener 40mm long | each | 85 | 2 |  | 2 |  |  |  |  | 2 | 170
6 | Cement, paint, sand etc. | each | 1 | 4.5 |  | 4.5 |  |  |  |  | 4.5 | 4.5
| Total | [10 empty] | 1620.4784
7 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 32.4096
1652.8879
8 | Installation,Testing and commissioning charges |  | 1 |  |  | 2204 |  | 2204 |  | 0 | 2204 | 2204
| WIREMAN G-1 | day | 1.25 | 579 |  | 723.75
| MASON G-2 | day | 0.75 | 579 |  | 434.25
| KHALLASI | day | 2 | 523 |  | 1046
2204
3856.8879
9 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 38.5689
3895.4568
10 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 584.3185
4479.7753
11 | Add 1% for WCT | [7 empty] | 1% |  |  | 44.7978
4524.5731
12 | Service Tax 6% | [7 empty] | 6% |  |  | 271.4744
4796.0475
4796.0475
| Rate per each | [10 empty] | 95.9209
96
Rate Analysis for Item no.
Supply and fixing of Telephone outlet (RJ11) with anodised GI box with front plate and plug in type telephone socket .
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | RJ11 TELEPHONE SOCKET |  | 1 | 178 | 30% | 124.6 |  | 124.6 |  |  | 124.6 | 124.6
2 | 1 MODULE BOX |  | 1 | 90 | 30% | 63 |  | 63 |  |  | 63 | 63
3 | 1MODULE FRONT PLATE |  | 1 | 142 | 30% | 99.4 |  | 99.4 |  |  | 99.4 | 99.4
| Total | [10 empty] | 287
4 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 5.74
292.74
5 | Installation,Testing and commissioning charges |  | 1 |  |  | 32.64 | 14.5% | 37.3728 |  | 0 | 37.3728 | 37.3728
| KHALLASI | day | 0.04 | 368 |  | 14.72
| WIREMAN G-1 | day | 0.04 | 448 |  | 17.92
32.64
330.1128
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 3.3011
333.4139
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 50.0121
383
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 3.83
386.83
8 | Service Tax 6% | [7 empty] | 6% |  |  | 22.98
406
406
Rate Analysis for Item no.
Supply and installation of 20 pair Krone connectors in junction box complete as required.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
(Analysis for 1 Number)
1 | 10 pair Krone junction box |  | 1 | 1500 | 30% | 1050 |  | 1050 | 14.5% | 152.25 | 1202.25 | 1202.25
1202.25
2 | Total | [7 empty] | 2% |  |  | 24.045
| Transportation, packing and forwarding charges | [10 empty] | 1226.295
3 | Installation,Testing and commissioning charges |  | 1 |  |  | 32.64 | 14.5% | 37.3728 |  | 0 | 37.3728 | 37.3728
| KHALLASI | day | 0.04 | 368 |  | 14.72
| WIREMAN G-1 | day | 0.04 | 448 |  | 17.92 | [5 empty] | 1263.6678
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 12.6367
[6 empty] | 32.64 | [5 empty] | 1276.3045
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 191.4457
1467.7501
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 14.6775
1482.4277
7 | Service Tax 6% | [7 empty] | 6% |  |  | 88.9457
1571.3733
| Rate per each | [10 empty] | 1571
| Say | [10 empty] | 1571
Rate Analysis for Item no.
Supply and laying of 2pair 0.5mm dia PVC insulated Copper conductor Telephone wire conforming to DOT Specification
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
(Analysis for 50 mtr)
1 | 2PAIR TELEPHONE CABLE Rs. |  | 53.03 | 9.2778 | 30% | 6.4944 |  | 6.4944 | 5% | 5 | 11.4944 | 609.5504
| Total | [10 empty] | 609.5504
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 12.191
621.7414
3 | Installation,Testing and commissioning charges |  | 50 |  |  | 11.02 |  | 11.02 |  | 0 | 11.02 | 551
| WIREMAN G-1 | day | 0.5 | 579 |  | 289.5
| KHALLASI | day | 0.5 | 523 |  | 261.5
551
1172.7414
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 11.7274
1184.4688
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 177.6703
1362.1391
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 13.6214
1375.7605
7 | Service Tax 6% | [7 empty] | 6% |  |  | 82.5456
1458.3062
| Rate per each | [10 empty] | 29.16
| Say | [10 empty] | 29
SUB HEAD - : FIRE ALARM SYSTEM
Rate Analysis for Item no.
Supply,Testing and commissioning of the following number of Loops Microprocessor based addressable type (EN / UL approved) Fire alarm control panel with Zonal Indications, supervised inputs, supervised and non-supervised outputs,Zener barriers, two way media converter / Signal booster for in / out network connectivity with OF cableand with battery Power pack as per specifications.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | a) 1 - Loop |  | 1 | 135000 | 10% | 121500 | 0% | 121500 | 14.5% | 17617.5 | 139117.5 | 139117.5
| Total | [10 empty] | 139117.5
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 2782.35
141899.85
Labour charges
3 | wire man , Grade 1 | DAY | 2 | 578 |  | 578 |  |  |  | 0 | 578 | 1156
4 | Khallasi | DAY | 2 | 523 |  | 523 |  |  |  | 0 | 523 | 1046
5 | Testing,by OEM Rep. | DAY | 3 | 2000 |  | 2000 |  |  |  | 0 | 2000 | 6000
150101.85
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 1501.0185
151602.8685
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 22740.4303
174343.2988
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 1743.433
176086.7318
9 | Service Tax 6% | [7 empty] | 6% |  |  | 10565.2039
186651.9357
| SAY | [10 empty] | 186652
Rate Analysis for Item no.
Supply & Fixing of reflective type self aligning motorizedBeam detector, receiver remote LED status indicator, sensitivity measurement filters and other mounting accessories with addressable monitor modules etc along with all fixing accessories.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | a) Beam detector |  | 1 | 26400 | 10% | 23760 | 0% | 23760 | 14.5% | 3445.2 | 27205.2 | 27205.2
| Total | [10 empty] | 27205.2
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 544.104
27749.304
Labour charges
3 | wire man , Grade 1 | DAY | 2 | 579 |  | 579 |  |  |  | 0 | 579 | 1158
4 | Khallasi | DAY | 2 | 523 |  | 523 |  |  |  | 0 | 523 | 1046
5 | Testing Engineer | DAY | 0.2 | 2000 |  | 2000 |  |  |  | 0 | 2000 | 400
30353.304
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 303.533
30656.837
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 4598.5256
35255.3626
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 352.5536
35607.9162
9 | Service Tax 6% | [7 empty] | 6% |  |  | 2136.475
37744.3912
| SAY | [10 empty] | 37744
Rate Analysis for Item no.
MULTI SENSOR DETECTORS
Supply installation, testing and commissioning of analog addressable type multi sensor (smoke / heat) photo electric detectors with LED indication lamp.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | analog addressable type multi sensor (smoke / heat) photo electric detectors with LED indication lamp. |  | 1 | 2580 | 10% | 2322 |  | 2322 | 14.5% | 336.69 | 2658.69 | 2658.69
| Total | [10 empty] | 2658.69
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 53.1738
2711.8638
Labour charges
3 | wire man , Grade 1 | DAY | 0.1 | 579 |  | 579 |  |  |  | 0 | 579 | 57.9
4 | Khallasi | DAY | 0.1 | 523 |  | 523 |  |  |  | 0 | 523 | 52.3
5 | Testing Engineer | DAY | 0.05 | 2000 |  | 2000 |  |  |  | 0 | 2000 | 100
2922.0638
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 29.2206
2951.2844
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 442.6927
3393.9771
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 33.9398
3427.9169
9 | Service Tax 6% | [7 empty] | 6% |  |  | 205.675
3633.5919
| SAY | [10 empty] | 3634
Rate Analysis for Item no.
ELECTRONIC HOOTERS:
Supply, Installation, Testing and commissioning of addressable Hooter cum strobe with loop sounder with all accessories and materials with control module & power supply unit.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | addressable Hooter cum strobe with loop sounder with all accessories and materials with control module & power supply unit. |  | 1 | 1920 | 10% | 1728 |  | 1728 | 14.5% | 250.56 | 1978.56 | 1978.56
| Total | [10 empty] | 1978.56
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 39.5712
2018.1312
Labour charges
3 | wire man , Grade 1 | DAY | 0.1 | 579 |  | 579 |  |  |  | 0 | 579 | 57.9
4 | Khallasi | DAY | 0.1 | 523 |  | 523 |  |  |  | 0 | 523 | 52.3
5 | Testing Engineer | DAY | 0.05 | 2000 |  | 2000 |  |  |  | 0 | 2000 | 100
2228.3312
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 22.2833
2250.6145
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 337.5922
2588.2067
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 25.8821
2614.0888
9 | Service Tax 6% | [7 empty] | 6% |  |  | 156.8453
2770.9341
| SAY | [10 empty] | 2771
Rate Analysis for Item no.
MANUAL CALL POINTS:
Supply and Installation of analogue addressable type Pull type Manual call Stations with monitor module
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | analogue addressable type Pull type Manual call Stations with monitor module |  | 1 | 2520 | 10% | 2268 |  | 2268 | 14.5% | 328.86 | 2596.86 | 2596.86
| Total | [10 empty] | 2596.86
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 51.9372
2648.7972
Labour charges
3 | wire man , Grade 1 | DAY | 0.1 | 579 |  | 579 |  |  |  | 0 | 579 | 57.9
4 | Khallasi | DAY | 0.1 | 523 |  | 523 |  |  |  | 0 | 523 | 52.3
5 | Testing Engineer | DAY | 0.05 | 2000 |  | 2000 |  |  |  | 0 | 2000 | 100
2858.9972
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 28.59
2887.5872
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 433.1381
3320.7252
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 33.2073
3353.9325
9 | Service Tax 6% | [7 empty] | 6% |  |  | 201.236
3555.1685
| SAY | [10 empty] | 3555
Rate Analysis for Item no.
FAULT ISOLATION MODULE:
Supply and installation fault isolator modules along with all fixing accessories.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | fault isolator modules along with all fixing accessories. |  | 1 | 2520 | 10% | 2268 |  | 2268 | 14.5% | 328.86 | 2596.86 | 2596.86
| Total | [10 empty] | 2596.86
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 51.9372
2648.7972
Labour charges
3 | wire man , Grade 1 | DAY | 0.1 | 579 |  | 579 |  |  |  | 0 | 579 | 57.9
4 | Khallasi | DAY | 0.1 | 523 |  | 523 |  |  |  | 0 | 523 | 52.3
5 | Testing Engineer | DAY | 0.05 | 2000 |  | 2000 |  |  |  | 0 | 2000 | 100
2858.9972
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 28.59
2887.5872
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 433.1381
3320.7252
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 33.2073
3353.9325
9 | Service Tax 6% | [7 empty] | 6% |  |  | 201.236
3555.1685
| SAY | [10 empty] | 3555
Rate Analysis for Item no.
CABLE:
Supplying, testing and commissioning of 1100V grade FIRE RESITANCE LOW SMOKE PVC copper conductor twisted pair cables.
a ) 25mm dia heavy gauge FRLS PVC conduit analysis 50MTR
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 25mm dia heavy gauge FRLS PVC conduit =(50+Wastage @ 5%) (3153/100Mtr) |  | 52.5 | 31.53 |  | 31.53 | 0% | 31.53 | 5% | 1.5765 | 33.1065 | 1738.0913
2 | 25mm dia PVC bends (619/100nos) |  | 4 | 6.19 |  | 6.19 | 0% | 6.19 | 5% | 0.3095 | 6.4995 | 25.998
3 | 25mm dia PVC coupler (302/100nos) |  | 5 | 3.02 |  | 3.02 | 0% | 3.02 | 5% | 0.151 | 3.171 | 15.855
4 | 25mm dia junction box (1920/100) |  | 5 | 19.2 |  | 19.2 | 0% | 19.2 | 5% | 0.96 | 20.16 | 100.8
5 | 25mm dia iron staples/saddles/screws |  | 30 | 2 |  | 2 | 0% | 2 | 5% | 0.1 | 2.1 | 63
6 | PVC fastener 40mm long |  | 30 | 1 |  | 1 | 0% | 1 | 5% | 0.05 | 1.05 | 31.5
| Total | [10 empty] | 1975.2443
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 39.5049
2014.7491
Labour charges
3 | Wire man , Grade 1 | DAY | 1.5 | 579 |  | 579 |  |  |  | 0 | 579 | 868.5
4 | Khallasi | DAY | 1.5 | 523 |  | 523 |  |  |  | 0 | 523 | 784.5
5 | Mason, Grade 2 | DAY | 1 | 579 |  | 579 |  |  |  | 0 | 579 | 579
4246.7491
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 42.4675
4289.2166
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 643.3825
4932.5991
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 49.326
4981.9251
9 | Service Tax 6% | [7 empty] | 6% |  |  | 298.9155
5280.8406
| Total for 50mtrs | [10 empty] | 5280.8406
| SAY 1Mtr | [10 empty] | 106
b ) Supply,laying,testing and commissioning of 2C x 1.5 sq.mm cable of 1.1 KV Grade XLPE , insulated, sheathed steel armoured with Copper Conductor Power Cables ( YWY ) should conform to IS 1554 ( Part I ). The rates quoted for laying shall include laying of cables on surface with saddles,screws etc. including material and labour charges etc complete as per site requirement.
b ) Twisted pair 2CX1.5 Sq.mm shielded FR insulated copper armoured conductor flexible wire analysis 50MTR
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 2CX1.5 Sq.mm shielded armoured twisted pair coper cable (=2776/100) |  | 52.5 | 27.76 | 0% | 27.76 | 0% | 27.76 | 5% | 1.388 | 29.148 | 1530.27
| Total | [10 empty] | 1530.27
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 30.6054
1560.8754
Labour charges
3 | Wire man , Grade 1 | DAY | 1.5 | 579 |  | 579 |  |  |  | 0 | 579 | 868.5
4 | Khallasi | DAY | 2 | 523 |  | 523 |  |  |  | 0 | 523 | 1046
3475.3754
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 34.7538
3510.1292
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 526.5194
4036.6485
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 40.3665
4077.015
9 | Service Tax 5.80% | [7 empty] | 5.8% |  |  | 236.4669
4313.4819
| Service Tax 6% | [7 empty] | 6% |  |  | 4313.4819
| SAY 1Mtr | [10 empty] | 86
Supply, fixing of exit light fixtures with 1.5Hrs battery backup. It shall be of standard size of 300mm Lx 180mm W, LED lamp with Ni-Mh / Ni-Cd Rechargeable battery 16-24Hrs recharging period with constant current charger and auto cut off facility to avoid over charging.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 300mm Lx 180mm W, LED lamp with Ni-Mh / Ni-Cd Rechargeable battery 16-24Hrs recharging period with constant current charger and auto cut off facility | No | 1 | 1607 | 10% | 1446.3 |  | 1446.3 | 14.5% | 209.7135 | 1656.0135 | 1656.0135
| Total | [10 empty] | 1656.0135
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 33.1203
1689.1338
3 | Labour charges
| Wire man , Grade 1 | Day | 0.2 | 579 |  | 579 |  |  |  |  | 579 | 115.8
| Khallasi | Day | 0.5 | 523 |  | 523 |  |  |  |  | 523 | 261.5
| Testing Engineer | Day | 0.1 | 2000 |  | 2000 |  |  |  |  | 2000 | 200
2066.4338
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 20.6643
2087.0981
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 313.0647
2400.1628
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 24.0016
2424.1645
7 | Service Tax 6% | [7 empty] | 6% |  |  | 145.4499
2569.6143
| SAY | [10 empty] | 2570
Rate Analysis for Item no.
PCC PANEL
Supply, installation, Testing and Commissioning of 3 phase and Neutral 415V 4 wire Free Standing Floor mounted MVpanel made out of 14 SWG MS sheet after seven tankprocess and painting with Epoxy powder coating. The panel shall consist of suitable rating TPN Aluminium busbar (at the rating of 0.8A/Sq.mm) supported with DMC/ SMC insulators and color coded with Heat shrinkable sleeves.TheMetering shall be provided as specified. The panel shall have Short circuit withstanding capacity of minimum 25KA and consist of the switchgear as mentioned below. The panel shall be got fabricated from manufacturers with CPRI Test certificate only. The PCC shall have atleast two spare cubicles of the maximum rating. The size of all PanelMounting Meters shall be 96X96mm. The Panels shall be mounted on U channels including supply and fixing of the same.
BUS BAR
TPN Alluminium busbar of 125A with 25 KA fault level capacity, mounted on non-hygroscopic, glass fibre reinforced insulators-1Set
INCOMER
100A, 25KA FP MCCBs (Thermal release) - 1no
2A, control fuse - 3 Nos.
RYB indicating lamps - 1 Set
100/5A, CL-1, 15VA CT's with tape wound - 3 nos.
KWH Meter
OUTGOINGS
63A, 10KA FP MCBs - 1no
40A, 10KA FP MCBs - 2no
32A, 10KA FP MCBs - 2nos
Two numbers of earthing terminals - one on each side of the panel with earth strip run inside the panel
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | Incoming:
| Incoming -: 100A,50 kA FP MCCB with thermal based release - 1 No. | each | 1 | 10364 | 30% | 7254.8 | 12.5% | 906.85 | 14.5% | 1183.4392 | 9345.0893 | 9345.0893
Busbars :125A TPN Aluminium Busbars - 1 set
2 | Outgoings :
| 63A 10 kA 4P MCBs -1 Nos | each | 1 | 2774 | 30% | 1941.8 | 0% | 0 | 14.5% | 281.561 | 2223.361 | 2223.361
| 40A 10 kA 4P MCBs -2 Nos | each | 2 | 2774 | 30% | 1941.8 | 0% | 0 | 14.5% | 281.561 | 2223.361 | 4446.722
| 32A 10 kA 4P MCBs -2 Nos | each | 2 | 1924 | 30% | 1346.8 | 0% | 0 | 14.5% | 195.286 | 1542.086 | 3084.172
3 | Metering For Incomer :
4 | 0-500V Digital Voltmeter with selector switch and MCB Control-1 set | each | 1 | 800 |  | 800 | 0% | 0 |  | 0 | 800 | 800
| Digital KWH meter | each | 1 | 1000 |  | 1000 | 0% | 0 |  | 0 | 1000 | 1000
| 100A Combined Digital Ammeter with resin cast CTs of ratio 100/5A, Class 1Accuracy and 15VA burden and selector switch -1 set | LS | 1 | 800 |  | 800 | 0% | 0 |  | 0 | 800 | 800
5 | LED Phase indication lamps with individuals MCBs and control with toggle switches- 1 set | Set | 1 | 1000 |  | 1000 | 0% | 0 |  | 0 | 1000 | 1000
6 | Inter connecting wires / strips : | LS | LS | [8 empty] | 0
7 | Busbar: 125A TPN Aluminium(1.61*110) | mtr | 1 | 17710 |  | 17710 | 0% | 0 |  | 0 | 17710 | 17710
8 | Cubicles :
| I/C MCCB | each | 1 | 5000 |  | 5000 | 0% | 0 |  | 0 | 5000 | 5000
| MCCBs/MCBs | each | 5 | 4000 |  | 4000 | 0% | 0 |  | 0 | 4000 | 20000
| Metering Cubile | LS | 1 | 4000 |  | 4000 | 0% | 0 |  | 0 | 4000 | 4000
| Overall chamber : | mtr | 1 | 10000 |  | 10000 | 0% | 0 |  | 0 | 10000 | 10000
| Total | [10 empty] | 79409.3442
| Transportation | [9 empty] | 2% | 1588.1869
9 | labour charges | [10 empty] | 80997.5311
TOTAL
| Wire man | Day | 1 | 579 | 0% | 579 |  | 0 |  | 0 | 579 | 579
| Khallasi | Day | 2 | 523 | 0% | 523 |  | 0 |  | 0 | 523 | 1046
| Beldar | Day | 2 | 523 | 0% | 523 |  | 0 |  | 0 | 523 | 1046
| Total | [10 empty] | 83668.5311
10 | Add 1% for Electricity charges | [9 empty] | 1% | 836.6853
| Total | [10 empty] | 84505.2164
11 | Add 15% ( 15% contractor's profit and overheads) | [9 empty] | 15% | 12675.7825
| Total | [10 empty] | 97180.9989
12 | Add 1% for WCT | [9 empty] | 1% | 971.81
| Total | [10 empty] | 98152.8089
13 | Add 5.8% Service tax | [9 empty] | 6% | 5889.1685
| Total | [10 empty] | 104041.9774
| Say | [10 empty] | 104042
Rate Analysis for Item no.
PCC PANEL
Supply, installation, Testing and Commissioning of 3 phase and Neutral 415V 4 wire Free Standing Floor mounted MVpanel made out of 14 SWG MS sheet after seven tankprocess and painting with Epoxy powder coating. The panel shall consist of suitable rating TPN Aluminium busbar (at the rating of 0.8A/Sq.mm) supported with DMC/ SMC insulators and color coded with Heat shrinkable sleeves.TheMetering shall be provided as specified. The panel shall have Short circuit withstanding capacity of minimum 25KA and consist of the switchgear as mentioned below. The panel shall be got fabricated from manufacturers with CPRI Test certificate only. The PCC shall have atleast two spare cubicles of the maximum rating. The size of all PanelMounting Meters shall be 96X96mm. The Panels shall be mounted on U channels including supply and fixing of the same.
BUS BAR
TPN Alluminium busbar of 125A with 25 KA fault level capacity, mounted on non-hygroscopic, glass fibre reinforced insulators-1Set
INCOMER
100A, 25KA FP MCCBs (Thermal release) - 1no
2A, control fuse - 3 Nos.
RYB indicating lamps - 1 Set
100/5A, CL-1, 15VA CT's with tape wound - 3 nos.
KWH Meter
OUTGOINGS
63A, 10KA FP MCBs - 1no
40A, 10KA FP MCBs - 3no
32A, 10KA FP MCBs - 2nos
Two numbers of earthing terminals - one on each side of the panel with earth strip run inside the panel
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | Incoming:
| Incoming -: 125A,50 kA FP MCCB with thermal based release - 1 No. | each | 1 | 11932 | 30% | 8352.4 | 12.5% | 1044.05 | 14.5% | 1362.4852 | 10758.9352 | 10758.9352
Busbars :160A TPN Aluminium Busbars - 1 set
2 | Outgoings :
| 63A 10 kA 4P MCBs -1 Nos | each | 1 | 2774 | 30% | 1941.8 | 0% | 0 | 14.5% | 281.561 | 2223.361 | 2223.361
| 40A 10 kA 4P MCBs -3 Nos | each | 3 | 2774 | 30% | 1941.8 | 0% | 0 | 14.5% | 281.561 | 2223.361 | 6670.083
| 32A 10 kA 4P MCBs -2 Nos | each | 2 | 1422 | 30% | 995.4 | 0% | 0 | 14.5% | 144.333 | 1139.733 | 2279.466
3 | Metering For Incomer :
4 | 0-500V Digital Voltmeter with selector switch and MCB Control-1 set | each | 1 | 800 |  | 800 | 0% | 0 |  | 0 | 800 | 800
| Digital KWH meter | each | 1 | 1000 |  | 1000 | 0% | 0 |  | 0 | 1000 | 1000
| 100A Combined Digital Ammeter with resin cast CTs of ratio 100/5A, Class 1Accuracy and 15VA burden and selector switch -1 set | LS | 1 | 800 |  | 800 | 0% | 0 |  | 0 | 800 | 800
5 | LED Phase indication lamps with individuals MCBs and control with toggle switches- 1 set | Set | 1 | 1000 |  | 1000 | 0% | 0 |  | 0 | 1000 | 1000
6 | Inter connecting wires / strips : | LS | LS | [8 empty] | 0
7 | Busbar: 125A TPN Aluminium(1.61*110) | mtr | 1 | 17710 |  | 17710 | 0% | 0 |  | 0 | 17710 | 17710
8 | Cubicles :
| I/C MCCB | each | 1 | 5000 |  | 5000 | 0% | 0 |  | 0 | 5000 | 5000
| MCCBs/MCBs | each | 6 | 4000 |  | 4000 | 0% | 0 |  | 0 | 4000 | 24000
| Metering Cubile | LS | 1 | 4000 |  | 4000 | 0% | 0 |  | 0 | 4000 | 4000
| Overall chamber : | mtr | 1 | 10000 |  | 10000 | 0% | 0 |  | 0 | 10000 | 10000
| Total | [10 empty] | 86241.8452
| Transportation | [9 empty] | 2% | 1724.8369
9 | labour charges | [10 empty] | 87966.6822
TOTAL
| Wire man | Day | 1 | 579 | 0% | 579 |  | 0 |  | 0 | 579 | 579
| Khallasi | Day | 2 | 523 | 0% | 523 |  | 0 |  | 0 | 523 | 1046
| Beldar | Day | 2 | 523 | 0% | 523 |  | 0 |  | 0 | 523 | 1046
| Total | [10 empty] | 90637.6822
10 | Add 1% for Electricity charges | [9 empty] | 1% | 906.3768
| Total | [10 empty] | 91544.059
11 | Add 15% ( 15% contractor's profit and overheads) | [9 empty] | 15% | 13731.6088
| Total | [10 empty] | 105275.6678
12 | Add 1% for WCT | [9 empty] | 1% | 1052.7567
| Total | [10 empty] | 106328.4245
13 | Add 5.8% Service tax | [9 empty] | 6% | 6379.7055
| Total | [10 empty] | 112708.13
| Say | [10 empty] | 112708
Rate Analysis for Item no.
c)Supply and fixing of 100 A FP MCCB, 25KA in sheet steel enclosure with all accessories etc., complete.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 100 A FP MCCB, 25KA |  | 1 | 10364 | 30% | 7254.8 |  | 7254.8 |  | 0 | 7254.8 | 7254.8
2 | MCCB ENCLOSURE |  | 1 | 2066 | 30% | 1446.2 |  | 1446.2 |  | 0 | 1446.2 | 1446.2
| Total | [10 empty] | 8701
3 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 174.02
8875.02
4 | S |  | 1 |  |  | 396.72 |  | 396.72 |  | 0 | 396.72 | 396.72
| WIREMAN G-1 | day | 0.24 | 579 |  | 138.96
| MASON G-2 | day | 0.12 | 579 |  | 69.48
| KHALLASI | day | 0.36 | 523 |  | 188.28
9271.74
5 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 92.7174
9364.4574
6 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 1404.6686
10769
7 | Add 1% for WCT | [7 empty] | 1% |  |  | 107.69
10876.69
8 | Service Tax 6% | [7 empty] | 6% |  |  | 646.14
11415
| SAY | [10 empty] | 11415
Rate Analysis for Item no.
c)Supply and fixing of 125 A FP MCCB, 25KA in sheet steel enclosure with all accessories etc., complete.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | MCCB ENCLOSURE |  | 1 | 3866 | 30% | 2706.2 |  | 2706.2 |  | 0 | 2706.2 | 2706.2
2 | 125 A FP MCCB, 25KA |  | 1 | 11932 | 30% | 8352.4 |  | 8352.4 |  | 0 | 8352.4 | 8352.4
| Total | [10 empty] | 11058.6
3 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 221.172
11279.772
4 | Installation,Testing and commissioning charges |  | 1 |  |  | 396.72 |  | 396.72 |  | 0 | 396.72 | 396.72
| WIREMAN G-1 | day | 0.24 | 579 |  | 138.96
| MASON G-2 | day | 0.12 | 579 |  | 69.48
| KHALLASI | day | 0.36 | 523 |  | 188.28
11676.492
5 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 116.7649
11793.2569
6 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 1768.9885
13562
7 | Add 1% for WCT | [7 empty] | 1% |  |  | 135.62
13697.62
8 | Service Tax 6% | [7 empty] | 6% |  |  | 813.72
14376
| SAY | [10 empty] | 14376
3.5CX25SQ.MM (Detail for 100Mtr) Ground
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5CX25SQ.MM Cable (M/s Finolex Make) | Mtr | 100 | 142.1 | 50% | 71.05 | 12.36% | 8.7818 | 5% | 3.9916 | 83.8234 | 8382.3369
2 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5=874+44(Wastage @5%)=918Nos | each | 918 | 5 | 0% | 5 |  |  |  |  | 5 | 4590
3 | Fine sand | Cum | 8.76 | 1590 | 0% | 1590 |  |  |  |  | 1590 | 13928.4
4 | Cable route markers | each | 2 | 225 | 0% | 225 |  |  |  |  | 225 | 450
| Total | [10 empty] | 27350.7369
| Transportation | [9 empty] | 2% | 547.0147
labour charges
| Wireman | Day | 1 | 579 | 0% | 579 |  |  |  |  | 579 | 579
| Khallasi | Day | 4 | 523 | 0% | 523 |  |  |  |  | 523 | 2092
| Total | [10 empty] | 30568.7516
| Add 1% for Electricity charges | [9 empty] | 1% | 305.6875
| Total | [10 empty] | 30874.4392
| Add 15% ( 15% contractor's profit and overheads) | [9 empty] | 15% | 4631.1659
| Excavation & back filling | Cum | 26.26 | 180 | 0% | 180 |  |  |  |  | 180 | 4726.8
| Total | [10 empty] | 40232.405
| Add 1% for WCT | [9 empty] | 1% | 402.3241
| Total | [10 empty] | 40634.7291
406.3473
| Service Tax 6% | [7 empty] | 6% |  | 6% | 24.3808
| Total | [10 empty] | 430.7281
| Say | [10 empty] | 431
Rate per Meter
3.5CX25SQ.MM (Detail for 100Mtr)cable run under hume pipe/ G I pipe/ cable Tray etc.,
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5C X 25Sq.mm Cable (M/s Finolex Make) | Mtr | 100 | 142.1 | 50% | 71.05 | 12.36% | 8.7818 | 5% | 3.9916 | 83.8234 | 8382.3369
| Gl saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 | 30% | 0.595 |  |  |  |  | 0.595 | 134.47
= 100/0.45 = 222 + 4 (Wastage @ 2%)
= 226 Nos
| Iron screws, 45 mm X 6 mm | each | 452 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 316.4
| Cement, paint, sand etc | each | 2 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 6.3
labour charges
| Wireman | Day | 1 | 579 | 0% | 579 |  |  |  |  | 579 | 579
| Khallasi | Day | 2 | 523 | 0% | 523 |  |  |  |  | 523 | 1046
| Total | [10 empty] | 10464.5069
| Add 1% for Electricity charges | [9 empty] | 1% | 104.6451
| Total | [10 empty] | 10569.152
| Add 15% ( 15% contractor's profit and overheads) | [9 empty] | 15% | 1585.3728
| Excavation & back filling | [10 empty] | 12154.5248
| Total | [9 empty] | 1% | 121.5452
| Add 1% for WCT | [10 empty] | 12276.07
| Total | [10 empty] | 122.7607
[11 empty] | 6% | 7.3656
| Service Tax 6% | [10 empty] | 130.1263
| Say | [10 empty] | 130
Rate per Meter
3.5CX35SQ.MM (Detail for 100Mtr) Ground
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5CX35SQ.MM Cable (M/s Finolex Make) | Mtr | 100 | 163.8 | 50% | 81.9 | 12.36% | 10.1228 | 5% | 4.6011 | 96.624 | 9662.3982
2 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5=874+44(Wastage @5%)=918Nos | each | 918 | 5 | 0% | 5 |  | 0 |  | 0 | 5 | 4590
3 | Fine sand | Cum | 8.76 | 1590 | 0% | 1590 |  | 0 |  | 0 | 1590 | 13928.4
4 | Cable route markers | each | 2 | 225 | 0% | 225 |  | 0 |  | 0 | 225 | 450
| Total | [10 empty] | 28630.7982
| Transportation | [9 empty] | 2% | 572.616
labour charges
| Wireman | Day | 1 | 579 | 0% | 579 |  | 0 |  | 0 | 579 | 579
| Khallasi | Day | 4 | 523 | 0% | 523 |  | 0 |  | 0 | 523 | 2092
| Total | [10 empty] | 31874.4142
| Add 1% for Electricity charges | [9 empty] | 1% | 318.7441
| Total | [10 empty] | 32193.1583
| Add 15% ( 15% contractor's profit and overheads) | [9 empty] | 15% | 4828.9737
| Excavation & back filling | Cum | 26.26 | 180 | 0% | 180 |  | 0 |  | 0 | 180 | 4726.8
| Total | [10 empty] | 41748.9321
| Add 1% for WCT | [9 empty] | 1% | 417.4893
| Total | [10 empty] | 42166.4214
421.6642
| Service Tax 6% | [9 empty] | 6% | 25.2999
| Total | [10 empty] | 446.9641
| Say | [10 empty] | 447
Rate per Meter
3.5CX35SQ.MM (Detail for 100Mtr)cable run under hume pipe/ G I pipe/ cable Tray etc.,
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5C X 35Sq.mm Cable (M/s Finolex Make) | Mtr | 100 | 163.8 | 50% | 81.9 | 12.36% | 10.1228 | 5% | 4.6011 | 96.624 | 9662.3982
| Gl saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 | 30% | 0.595 |  |  |  |  | 0.595 | 134.47
= 100/0.45 = 222 + 4 (Wastage @ 2%)
= 226 Nos
| Iron screws, 45 mm X 6 mm | each | 452 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 316.4
| Cement, paint, sand etc | each | 2 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 6.3
labour charges
| Wireman | Day | 1 | 579 | 0% | 579 |  |  |  |  | 579 | 579
| Khallasi | Day | 2 | 523 | 0% | 523 |  |  |  |  | 523 | 1046
| Total | [10 empty] | 11744.5682
| Add 1% for Electricity charges | [9 empty] | 1% | 117.4457
| Total | [10 empty] | 11862.0139
| Add 15% ( 15% contractor's profit and overheads) | [9 empty] | 15% | 1779.3021
| Excavation & back filling | [10 empty] | 13641.316
| Total | [9 empty] | 1% | 136.4132
| Add 1% for WCT | [10 empty] | 13777.7291
| Total | [10 empty] | 137.7773
[11 empty] | 6% | 8.2666
| Service Tax 6% | [10 empty] | 146.0439
| Say | [10 empty] | 146
Rate per Meter
3.5CX50SQ.MM (Detail for 100Mtr) Ground
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5CX50SQ.MM Cable (M/s Finolex Make) | Mtr | 100 | 226.9 | 50% | 113.45 | 12.36% | 14.0224 | 5% | 6.3736 | 133.846 | 13384.6041
2 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5=874+44(Wastage @5%)=918Nos | each | 918 | 5 | 0% | 5 |  |  |  |  | 5 | 4590
3 | Fine sand | Cum | 8.76 | 1590 | 0% | 1590 |  |  |  |  | 1590 | 13928.4
4 | Cable route markers | each | 2 | 225 | 0% | 225 |  |  |  |  | 225 | 450
| Total | [10 empty] | 32353.0041
| Transportation | [9 empty] | 2% | 647.0601
labour charges
| Wireman | Day | 1 | 579 | 0% | 579 |  |  |  |  | 579 | 579
| Khallasi | Day | 4 | 523 | 0% | 523 |  |  |  |  | 523 | 2092
| Total | [10 empty] | 35671.0642
| Add 1% for Electricity charges | [9 empty] | 1% | 356.7106
| Total | [10 empty] | 36027.7748
| Add 15% ( 15% contractor's profit and overheads) | [9 empty] | 15% | 5404.1662
| Excavation & back filling | Cum | 26.26 | 180 | 0% | 180 |  |  |  |  | 180 | 4726.8
| Total | [10 empty] | 46158.741
| Add 1% for WCT | [9 empty] | 1% | 461.5874
| Total | [10 empty] | 46620.3285
466.2033
| Service Tax 6% | [9 empty] | 6% | 27.9722
| Total | [10 empty] | 494.1755
| Say | [10 empty] | 494
Rate per Meter
3.5CX50SQ.MM (Detail for 100Mtr)cable run under hume pipe/ G I pipe/ cable Tray etc.,
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5C X 50Sq.mm Cable (M/s Finolex Make) | Mtr | 100 | 226.9 | 50% | 113.45 | 12.36% | 14.0224 | 5% | 6.3736 | 133.846 | 13384.6041
2 | Gl saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 | 30% | 0.595 |  |  |  |  | 0.595 | 134.47
= 100/0.45 = 222 + 4 (Wastage @ 2%)
= 226 Nos
3 | Iron screws, 45 mm X 6 mm | each | 452 | 1 | 30% | 0.7 |  |  |  |  | 0.7 | 316.4
4 | Cement, paint, sand etc | each | 2 | 4.5 | 30% | 3.15 |  |  |  |  | 3.15 | 6.3
5 | labour charges
| Wireman | Day | 1 | 579 | 0% | 579 |  | 0 |  | 0 | 579 | 579
| Khallasi | Day | 2 | 523 | 0% | 523 |  | 0 |  | 0 | 523 | 1046
| Total | [10 empty] | 15466.7741
6 | Add 1% for Electricity charges | [9 empty] | 1% | 154.6677
| Total | [10 empty] | 15621.4418
7 | Add 15% ( 15% contractor's profit and overheads) | [9 empty] | 15% | 2343.2163
| Excavation & back filling | [10 empty] | 17964.6581
| Total | [9 empty] | 1% | 179.6466
8 | Add 1% for WCT | [10 empty] | 18144.3047
| Total | [10 empty] | 181.443
[11 empty] | 6% | 10.8866
9 | Service Tax 6% | [10 empty] | 192.3296
| Say | [10 empty] | 192
Rate per Meter
Rate Analysis for Item no.
3.5C X25 Sq.mm
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5 C 25 sqmm GLANDS |  | 1 | 289.6 | 20% | 231.68 |  | 231.68 | 14.5% | 33.5936 | 265.2736 | 265.2736
2 | 25 sqmm LUG |  | 1 | 6.12 | 20% | 4.896 |  | 4.896 | 14.5% | 0.70992 | 5.6059 | 5.6059
3 | 16sqmm LUG |  | 3 | 3.01 | 20% | 2.408 |  | 2.408 | 14.5% | 0.34916 | 2.7572 | 8.2715
| Total | [10 empty] | 279.151
4 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 5.583
284.734
5 | Installation,Testing and commissioning charges |  | 1 |  |  | 110.2 |  | 110.2 |  | 0 | 110.2 | 110.2
| WIREMAN G-1 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.1 | 523 |  | 52.3 | [5 empty] | 394.934
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 3.9493
398.8834
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 59.8325
458.7159
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 4.5872
463.303
9 | Service Tax 6% | [7 empty] | 6% |  |  | 27.7982
491.1012
491
Rate Analysis for Item no.
3.5C X35 Sq.mm
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5 C 35 sqmm GLANDS |  | 1 | 289.6 | 20% | 231.68 |  | 231.68 | 14.5% | 33.5936 | 265.2736 | 265.2736
2 | 35sqmm LUG |  | 1 | 8.97 | 20% | 7.176 |  | 7.176 | 14.5% | 1.0405 | 8.2165 | 8.2165
3 | 16 sqmm LUG |  | 3 | 3.01 | 20% | 2.408 |  | 2.408 | 14.5% | 0.34916 | 2.7572 | 8.2715
| Total | [10 empty] | 281.7616
4 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 5.6352
287.3968
5 | Installation,Testing and commissioning charges |  | 1 |  |  | 110.2 |  | 110.2 |  | 0 | 110.2 | 110.2
| WIREMAN G-1 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.1 | 523 |  | 52.3 | [5 empty] | 397.5968
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 3.976
401.5728
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 60.2359
461.8087
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 4.6181
466.4268
9 | Service Tax 6% | [7 empty] | 6% |  |  | 27.9856
494.4124
494
Rate Analysis for Item no.
3.5C X50Sq.mm
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 3.5 C X 50sqmm GLANDS |  | 1 | 425.6 | 20% | 340.48 |  | 340.48 | 14.5% | 49.3696 | 389.8496 | 389.8496
2 | 50 sqmm LUG |  | 1 | 13.94 | 20% | 11.152 |  | 11.152 | 14.5% | 1.617 | 12.769 | 12.769
3 | 25 sqmm LUG |  | 3 | 6.12 | 20% | 4.896 |  | 4.896 | 14.5% | 0.70992 | 5.6059 | 16.8178
| Total | [10 empty] | 419.4364
4 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 8.3887
427.8251
5 | Installation,Testing and commissioning charges |  | 1 |  |  | 110.2 |  | 110.2 |  | 0 | 110.2 | 110.2
| WIREMAN G-1 | day | 0.1 | 579 |  | 57.9
| KHALLASI | day | 0.1 | 523 |  | 52.3 | [5 empty] | 538.0251
6 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 5.3803
543.4054
7 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 81.5108
624.9162
8 | Add 1% for WCT | [7 empty] | 1% |  |  | 6.2492
631.1653
9 | Service Tax 6% | [7 empty] | 6% |  |  | 37.8699
669.0353
669
Rate Analysis for Item no.
Providing GI Earth station, with 40 mm Class B GI pipe at 2500mm depth including construction of brick pedestal, providing meshed funnel,CI cover and other civil Engineering works, spreading a homogenous mixture of salt,charcoal around the pipe etc,completely as per IS3043,1987 or latest revision.
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
Cost for one Set
A1 MATERIAL
1 | 40mm dia. G.I.pipe, medium class | Meter | 2.5 | 225.92 |  | 225.92 |  |  |  | 0 | 225.92 | 564.8
2 | Funnel, G.I. nuts and through bolts, G.I. Washers | Each | 1 | 37.5 |  | 37.5 |  |  |  | 0 | 37.5 | 37.5
3 | locking arrangements with hinged cover plate | Each | 1 | 248.05 |  | 248.05 |  |  |  | 0 | 248.05 | 248.05
4 | 40mm to 20mm reducer | Each | 1 | 36 |  | 36 |  |  |  | 0 | 36 | 36
5 | Drilling of 46Nos 12mm dia holles on G.I. pipe | Each | 1 | 270 |  | 270 |  |  |  | 0 | 270 | 270
6 | Charcoal | kg | 64 | 9 |  | 9 |  |  |  | 0 | 9 | 576
7 | salt | kg | 5 | 8 |  | 8 |  |  |  | 0 | 8 | 40
B LABOUR
8 | wireman, Grade 1 | Day | 0.5 | 579 | [7 empty] | 289.5
9 | Khallasi | Day | 0.5 | 523 | [7 empty] | 261.5
10 | Excavation | cum | 2.5 | 85 | [7 empty] | 212.5
11 | Brick work in cement mortar | Ls | 1 | 117 | [7 empty] | 117
2652.85
12 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 26.5285
2679.3785
13 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 401.9068
3081
14 | Add 1% for WCT | [7 empty] | 1% |  |  | 30.81
3111.81
15 | Service Tax 6% | [7 empty] | 6% |  |  | 184.86
3266
Rate Analysis for Item no.
b) Supply and laying of following size strips including including all necessary inter connections with earth station and equipments.
i) 25 mm X 5mm Hot dip GI strip
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 25x5mm Hot dip GI Strip (1.1 kg/mtr) | KG | 33 | 65 | 0% | 65 |  | 0 | 14.5% | 9.425 | 74.425 | 2456.025
| Total | [10 empty] | 2456.025
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 49.1205
2505.1455
B LABOUR
1 | wireman, Grade 1 | Day | 0.125 | 579 | [7 empty] | 72.375
3 | Khallasi | Day | 0.125 | 523 | [7 empty] | 65.375
| Excavation | cum | 2.7 | 200 | [7 empty] | 540
| Soldering joint | No | 1 | 10 | [7 empty] | 10
3192.8955
4 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 31.929
3224.8245
5 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 483.7237
3708.5481
6 | Add 1% for WCT | [7 empty] | 1% |  |  | 37.0855
3745.6336
7 | Service Tax 6% | [7 empty] | 6% |  |  | 224.738
3970.3716
8 | Rate per each | [10 empty] | 132.3457
| Say | [10 empty] | 132
Rate Analysis for Item no.
Providing,laying and fixing following Dia RCC pipe NP2 Class (Light duty) in ground complete with RCC collars. jointing with cement mortar 1:2 (1 cement : 2 fine sand) including with trenching (75 cm deep)and re-filling etc.as required
S.NO | DESCRIPTION | UNIT | QTY | LP | DIS | LPRate | ED | EDRate | Taxes | Taxesrate | T.RATE | AMOUNT
1 | 100 MM Dia RCC PIPE NP2 CLASS | Mtr | 1 | 313 | 0% | 313 |  | 0 | 14.5% | 45.385 | 358.385 | 358.385
| Total | [10 empty] | 358.385
2 | Transportation, packing and forwarding charges | [7 empty] | 2% |  |  | 7.1677
365.5527
B LABOUR
3 | wireman, Grade 1 | Day | 0.5 | 579 | [7 empty] | 289.5
4 | Khallasi | Day | 0.75 | 523 | [7 empty] | 392.25
5 | Excavation | cum | 2.7 | 200 | [7 empty] | 540
6 | Soldering joint | No | 1 | 10 | [7 empty] | 10
1597.3027
7 | Add 1% for Electricity Charges | [7 empty] | 1% |  |  | 15.973
1613.2757
8 | Add 15% Contractors profit | [7 empty] | 15% |  |  | 241.9914
1855
9 | Add 1% for WCT | [7 empty] | 1% |  |  | 18.55
1873.55
10 | Service Tax 6% | [7 empty] | 6% |  |  | 111.3
1985

## BASIC RATES (hidden)
BASIC RATES OF E & M
S.NO | DESCRIPTION | UNIT | BASE PRICE(Rs)
A | PVC Insluated Copper FRLS wires (Make -Finolex )
1 | 1.5sq.mm Copper wire Rs.1330 /90 Mtrs | Rmt | 14.7778
2 | 2.5sq.mm copper wires Rs.2120/90 Mtrs | Rmt | 23.5556
3 | 4sq.mm copper wires Rs.3080 /90 Mtrs | Rmt | 34.2222
4 | 6sq.mm copper wires Rs4755/90 Mtrs | Rmt | 52.8333
5 | 10 sq.mm Heavy duty copper wires Rs7640/100 Mtrs | Rmt | 76.4
6 | 10 pair 0.5mm dia telephone cable Rs.3900 /90 Mtrs | Rmt | 43.3333
7 | 2 pair 0.5mm dia telephone cable Rs.900/90 Mtrs | Rmt | 9.2778
B | Conduits, Junction Boxes & Misc (Make - Sudhakar)
1 | 25mm dia Heavy duty PVC Conduit | Rmt | 31.53
2 | 25mm dia deep junction boxes | No | 26.47
3 | 25mm dia heavy duty Bends | No | 8.85
4 | 32mm dia Heavy duty PVC Conduit | Rmt | 50.14
5 | 32mm dia deep junction boxes | No | 40.41
6 | 32mm dia heavy duty Bends | No | 19.38
7 | 40mm dia Heavy duty PVC Conduit | Rmt | 66.88
8 | 40mm dia deep junction boxes | No | 44.34
9 | 40mm dia heavy duty Bends | No | 28.75
C | Metal boxs (Make -legrand)
1 | Metal box (1/2 module) | No | 90
2 | Metal box (3 module) | No | 90
3 | Metal box (4 module) | No | 118
4 | Metal box (6 module) | No | 186
5 | Metal box (8 module) | No | 216
6 | Metal box (12 module) | No | 324
D | Front plates with Cover (Make -legrand)
1 | switch plate (1module) | No | 142
2 | switch plate (2module) | No | 150
3 | switch plate (3module) | No | 164
4 | switch plate (4module) | No | 14
5 | switch plate (6module) | No | 322
6 | switch plate (8module) | No | 344
7 | switch plate (12module) | No | 428
E | Switches, Sockets & outlets (Make -legrand)
1 | 6A switch (1 module) | No | 140
2 | 6A 2way switch (1 module) | No | 186
3 | 16 A switch (1 module) | No | 244
4 | 6A 5Pin socket (2 module) | No | 260
5 | 6A/16 A socket (2 module) | No | 358
6 | 100 W Electronic regulator (2 module) | No | 798
7 | RJ11 Telephone socket (1 module) | No | 178
8 | 6A Bell push (1 module) | No | 204
9 | Buzzer | No | 966
F | MCB,MCCB,RCBO& Distrubtion Boards (Make -Legrand)
1 | 4WAY TPN MCB DB | No | 5526
2 | 4 Way VTPN MCB DB | No | 10482
3 | 125A, 4P, 25KA MCCB | No | 11932
4 | 100A, 4P, 25KA MCCB | No | 10364
5 | 40A FP RCBO, 100mA | No | 5758
6 | 63A FP MCB | No | 2774
7 | 40A 4P MCB | No | 2774
8 | 32A FP MCB | No | 1924
9 | 32A TP MCB | No | 1422
10 | 20 DP MCB | No | 872
11 | 6-32 A SP MCB | No | 294
12 | 32 A 3p+N+e METAL CLAD SOCKET | No | 5580
13 | 20A Metal clad socket and plug | No | 2012
14 | Enclosure for 100A FP MCCB | No | 2066
15 | Enclosure for 125A FP MCCB | No | 3866
G | Light fixtures Wipro, Philips, Bajaj, Crompton
1 | a) 33W Recess Mounted 2ft x 2ft LED Luminaire with Diffuser similar to CAT NO: CRCO10R036HP57G1, WIPRO MAKE | No | 6190
2 | b) 12W Recess mounted circular LED downlighter ( CAT NO: CRDL11R017HP57 WIPRO MAKE | No | 2250
3 | a) 139.2 W Radial Prime LED Highbay similar CAT NO. LH09-172- 060-50-G1 WIPRO MAKE | No | 27550
H | FANS-HAVELS
1 | 1200mm Ceiling Fan | No | 2275
2 | 300 mm Exhust Fan | No | 3615
I | CABLES- FINOLEX XLPE insulted 1.1Kv grade Al Cables
| a)3C X 4 Sq.mm Copper | Rmt | 142.7
| b)4C X 10 Sq.mm Aluminium | Rmt | 83.1
| c) 4C X 16 Sq.mm Aluminium | Rmt | 116.8
| d) 3.5C X25 Sq.mm Aluminium | Rmt | 142.1
| e) 3.5C X35Sq.mm Aluminium | Rmt | 163.8
| f) 3.5C X50Sq.mm Aluminium | Rmt | 226.9
J | Single compression Gland - Comet
1 | a)3C X 4 Sq.mm Copper 1" | No | 174.1
2 | b)4C X 10 Sq.mm Aluminium 1 1/4" | No | 289.6
3 | c) 4C X 16 Sq.mm Aluminium 1 1/4" | No | 289.6
4 | d) 3.5C X25 Sq.mm Aluminium 1 1/4" | No | 289.6
5 | e) 3.5C X35Sq.mm Aluminium 1 1/4" | No | 289.6
6 | f) 3.5C X50Sq.mm Aluminium 1 1/2" | No | 425.6
K | LUGS - Dowels
1 | 50 sqmm | No | 13.94
2 | 35 sqmm | No | 8.97
3 | 25sqmm | No | 6.12
4 | 16 sqmm | No | 2.67
5 | 10 sqmm | No | 3.01
6 | 4sqmm | No | 6.27
L | EARTHING
1 | Cu. Strip | Kg | 625
2 | GI strip | Kg | 65

## Receway est
S No. | Description | QTY | Unit | Rate | Amount
32 ii) | Raceway in flooring :
ii) S.I.T.C of GI Raceways with fixing brackets and all necessary accessories etc., complete. Legrand
| a) 150mm x 38mm 1 compartment | 120 | Meter
| b) 225mm X 38mm 3 Compartment | 120 | Meter
| c) 300mm X 38mm 3 Compartment | 120 | Meter
iii) S.IT.C. of Height adjustable raceway junction box with flyover for direct access to cables at intersection while maintaining perfect separation and 90 deg cross over between data and power cables with all fixing accessories etc., complete. Legrand
| a) 225mm X 225mm X 65-90mm with flyover | 10 | No
| b) 300mm X 300mm X 65-90mm with flyover | 10 | No
| c) 400mm X 400mm X 65-90mm with flyover | 10 | No

## ABSTRACT
ABSTRACT OF INTERIOR, CIVIL, ELECTRICAL, AC, IP PHONES, SECURITY CAMERAS, SECURITY ACCESS CONTROL, SOUND SYSTEM, FIRE ALARM AND SPRINKLER SYSTEMS FOR SBI LIFE REGIONAL OFFICE AT VIJAYAWADA.
S no. | Description | Amount | Remarks
1 | INTERIOR WORKS
2 | CIVIL WORKS
3 | ELECTRICAL WORKS ( INCLUDING IP PHONES, SECURITY & SOUND SYSTEMS)
4 | SPRINKLER SYSTEM
5 | FIRE ALARM & DETECTION SYSTEM
6 | HVAC WORKS
GRAND TOTAL